## USER GUIDE - SO
EDM Storm Overflow Annual Return: Quick User Guide
!! See separate User Guide in Word format for further detail !!
General Guidance:
- The EDM annual return 2021 should list all storm overflows with spills to the environment (permitted/unpermitted with permit application made), irrespective of whether they are currently have EDM installed or existing EDM permit condition.
- The EDM annual return 2021 should include data for (1) All storm overflows with an existing EDM permit condition, and (2) All storm overflows with EDM intalled through the WINEP/AMP7 EDM programme, with or without a current EDM permit condition. Data should also be included for overflows where a permit has been applied for by the WaSC but not yet issued.
- WaSCs are expected to provide EDM data for overflows without a current EDM requirement (e.g. not secured through the WINEP nor with a permit requirement), where they deem this data accurate & representative of spills
- Reported spill data (count & duration) should be considered reliable, verified and an accurate representation of the spills that occurred during the reporting period. Data that is known to be erroneous should not be reported on. See main User Guide (Word document) for more information and examples.
- Base information (e.g. EA permit reference, site name, Outlet NGR etc.) on overflows must directly match the Environment Agency (EA) Consents Database (see "Resources" below).
- Where EDM reporting operability is <90% (Column Q) subsequent columns Primary Reason (Column R) and Action Taken / Planned (Column S) must be completed.
- If spill count data (column P + valid data in previous years) exceeds thresholds in the SOAF guidance then columns T, U, V (Spill Frequency - operational & planning info) must be completed.
- A number of columns are "do once"; the data are not expected to change year on year. These headings are highlighted in grey below. Data in remaining columns are expected to change each year. These headings are highlighted in light green below.
- Water Framework Directive (WFD) data in columns I & J have been pre-populated by the EA using the Outlet NGR provided by WaSCs [November 2021] in column H.
- Any additional overflows not previously provided, or newly-reconciled Consents Database permit references must be submitted by WaSCs to the EA by Friday 21 January 2022. The EA will then identify the relevant WFD information & return to WaSCs on Friday 28 January ahead of final submission by WaSCs the following month.
Resources:
- Environment Agency national consents database: |  | Consented Discharges to Controlled Waters with Conditions - data.gov.uk
(Note the EA Consents Database is updated quarterly on .gov.uk)
- Environment Agency Risk-Based Approach to the Monitoring of Storm Discharges (September 2013)
- Environment Agency Storm Overflow Assessment Framework (June 2018): |  |  | Storm Overflow Assessment Framework
Guide to columns & drop-down selection:
Water Company Name | (Column A)
Site Name (EA Consents Database) | (Column B)
- Site name that matches exactly with column "Discharge_Site_Name" on EA consents database
Site Name (WaSC Operational Name) | (Column C)
- Site name used by the WaSC for operational reasons. The EA Consents Database Site Name must be provided in column B - the WaSC site name is not a substitute
- Column C is optional
EA Consents Database Permit Reference | (Column D)
- As shown in column "Permit Number" on EA Consents Database. NB: this may occassionally differ from number shown on actual permit or WaSC URN/folio
WaSC Supplementary Permit Ref. | (Column E)
- WaSC reference number for permitted overflow. The EA Consents Database permit reference must be provided in column D - the WaSC permit reference is not a substitute
- Column E is optional
Activity reference | (Column F)
- Listed on new format permits under Schedule 1 – “Operations” (e.g. A1 / A2 etc.)
- Listed on old format permits under Schedule conditions (e.g. Schedule No. A.115K/00-01)
- NB: This is not the same as columns “DISCHARGE_SITE_TYPE_CODE” or “DSI_TYPE_DESCRIPTION” on EA consents database
Storm discharge asset type | (Column G)
- As detailed in risk-based approach to EDM document (2013)
- See the more detailed User Guide (Word format) for a table of definitions (page 6)
- NB: This is not the same as columns “DISCHARGE_SITE_TYPE_CODE” or “DSI_TYPE_DESCRIPTION” on EA consents database
Drop-down options Column G:
SO on sewer network | On network - storm overflow. Can be direct or associated with a network storm tank. Not associated with pumping station
Storm discharge at pumping station | On network - pumping station
Inlet SO at WwTW | Storm overflow (direct to the environment) permitted as part of a WwTW permit. Exception is a storm tank - see note on next row
Storm tank at WwTW | Storm overflow via a storm tank, permitted as part of a WwTW permit. Note this can be physically remote from the WwTW
Other storm discharge asset type | Any storm overflow that does not clearly align with the four categories above. These may be used to devlop future drop-down categories.
Outlet discharge NGR (Consents Database) | (Column H)
- This is the actual discharge point to the environment.
- Listed on EA consents database as “OUTLET_GRID_REF”. This is the reference to use
- Also listed on new format permits under Schedule 3 - "Discharge Point NGR"
- Also listed on old format permits under "Place of Discharge"
- NB: This is not the same as columns “DISCHARGE_NGR” (discarhge site NGR) or “EFFLUENT_GRID_REF” (effluent monitoring NGR) on EA consents database
WFD Waterbody ID (Cycle 2) | (Column I)
- Identification number of WFD waterbody at the discharge point (as per Cycle 2)
- Prefixed with "GB…"
- Pre-populated by EA using outlet discharge NGR (column H). Any further overflows requiring the EA to populate WFD information must be submitted to the EA by Friday 21 January 2022
WFD Waterbody Catchment Name (Cycle 2) | (Column J)
- Name of WFD waterbody catchment at the discharge point (as per Cycle 2)
- NB: This is not the same as "CATC_NAME" on EA consents database
- Pre-populated by EA using outlet discharge NGR (column H). Any further overflows requiring the EA to populate WFD information must be submitted to the EA by Friday 21 January 2022
Receiving Water / Environment - common name (Consents Database) | (Column K)
- Listed on EA consents database under "RECEIVING_WATER" NB: this may differ from receiving water shown on actual permit
- Also listed on new format permits under Schedule 3 - "Discharge Point"
- Also listed on old format permits under "Place of Discharge"
Shellfishery | (Column L)
- Populate for storm overflows that have Shellfish Water EDM requirements
Bathing Beach | (Column M)
- Populate for storm overflows that have Bathing Water EDM requirements
Initial EDM commission date | (Column N)
- Date EDM commissioned; the date data can be expected from the EDM
- See the more detailed User Guide (Word format) for more detailed table of definitions (page 7)
- Note: Installation date may precede commissioned date
Drop-down options Column M:
Installed but not yet commissioned | Installed in current reporting year but data not yet expected
Commissioned in 2020 - full year data expected | Installed in previous reporting year
Commissioned in 2019 - full year data expected | Installed in previous reporting year
Commissioned in 2018 - full year data expected | Installed in previous reporting year
Commissioned in 2017 - full year data expected | Installed in previous reporting year
Commissioned in 2016 - full year data expected | Installed in previous reporting year
Commissioned pre-2016 - full year data expected | Installed in previous reporting year
Jan 2021
Feb 2021
Mar 2021
April 2021
May 2021
June 2021
July 2021
August 2021
September 2021
October 2021
November 2021
December 2021
EDM to be installed by December 2023 | EDM not yet installed
Total Duration (hr) of all spills | (Column O)
- Total spill duration prior to processing through the 12-24h count method
Counted spills using 12-24h count method | (Column P)
- Spill count post-processed through the 12-24h count method
EDM Operation - % reporting period EDM operational | (Column Q)
- Based on Initial Commissioning Date (Column M) e.g. commissioned in July of reporting year then period Jul-Dec would be 100%; if commissioned in previous reporting year then period Jan-Dec would be 100%
- e.g. commissioned in September of reporting year then 100% reporting period would be Sep.-Dec.
- e.g. commissioned in any previous reporting year then 100% reporting period would be Jan.-Dec.
- See the more detailed User Guide (Word format) for further information & examples
EDM Operation - Reporting % - Primary Reason <90% | (Column R)
- Core reason why EDM may not have been operational <90% of period (Column Q)
- Select primary reason only
- Category must be selected when period of EDM operation (column Q) is less than 90%. Optional to complete this column when period of EDM operation is 90% or over
- See the more detailed User Guide (Word format) for table of definitions (page 8)
Drop-down options Column R:
Access - Unable to retrieve data from non-telemetry data logger (NB: not to be used for delayed access to fix existing fault) | When access causes inability to retrieve data; e.g. landowner permission. Consider core reason – if caused by poor installation or design then select “Installation set-up/design issue” category instead. Not to be used for delayed access t fix existing operational fault
Capital / maintenance works affect EDM operation | Where planned works affect EDM operation. Consider core reason – if caused by poor installation or design then select “Installation set-up/design issue” category instead
Comms failure / issue | Any part of communication failure; e.g. intermittent signal or antenna damage. Consider core reason – if caused by poor installation or design then select “Installation set-up/design issue” category instead. Similar if comms loss caused by power failure – select “Power failure / issue” instead
EDM not yet installed | E.g. not yet scheduled for installation, or installation not currently feasible
EDM installed - not yet commissioned | E.g. installed after reporting period. E.g. installed within reporting period but data not yet calibrated
Installation set-up/design issue | When installation or design (e.g. choice of location) affects EDM operability. E.g. Original design location cannot distinguish between two overflows & original EDM needs to be relocated to more representative point. E.g. Original design location affected by river ingress & EDM requires relocation. E.g. Alternative monitor type required
Power failure / issue | Any part of power failure; e.g. loss of mains supply / battery fault. Consider core reason – if caused by cutting through cable then select “Capital / maintenance works” category instead
Sensor failure / issue | Any part of sensor failure; e.g. water ingress to connection between sensor & logger. Consider core reason – if water ingress caused by poor choice of location for installation & requires adjustment then select “Installation set-up/design issue” category instead
Telemetry or data archiving failure / issue | Any part of telemetry failure; e.g. dial-in or storage/sending of data problems. Consider core reason – if archiving problem caused by power fault or incorrect installation then use “Power failure / issue” or ”Installation set-up/design issue” categories respectively. Similar if data transfer caused by intermittent signal – select “Comms failure / issue” instead
No longer operational as an overflow - permit revoked or to be revoked
Reporting % - Action taken / planned - Status & Timeframe | (Column S)
- Indicate whether action has already been taken / is planned to be taken, or whether there is an ongoing investigation to identify the appropriate action
- Which month this activity was completed / is planned
- See the more detailed User Guide (Word format) for table of definitions (page 10)
Drop-down options Column R:
Scheduled | Appropriate operational action to address <90% EDM operation is planned
Resolved - January | Appropriate operational action has already been taken & issue affecting EDM operation resolved
Resolved - Feburary | As above
Resolved - March | As above
Resolved - April | As above
Resolved - May | As above
Resolved - June | As above
Resolved - July | As above
Resolved - August | As above
Resolved - September | As above
Resolved - October | As above
Resolved - November | As above
Resolved - December | As above
N/A - Ongoing investigation | Appropriate action not yet identified
N/A - EDM to be installed by December 2023 | Use when selection in Column R is “EDM not yet installed”
Spill Frequency - Operational Review Outcome - Primary Reason | (Column T)
- Core reason for spill count (Column P)
- Select primary reason only
- Category must be selected when spill frequency exceeds SOAF threshold (using column P + data from previous years)
- See the more detailed User Guide (Word format) for table of definitions (page 10)
Drop-down options Column T:
Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue | Spill frequency primarily caused by maintenance issue; e.g. roots causing channel restriction e.g. blocked screens causing premature spills
Performance - Sewer collapse (partial / full) - infrastructure issue | Spill frequency primarily caused by infrastructure issue; e.g. partial collapse of sewer
Performance - Groundwater inundation | Groundwater inundation is primary reason for spills; e.g. GW inundation in chalk catchment causing high spill frequency
Performance - Infiltration | High spill frequency caused by infiltration. Requires investment to infrastructure to resolve
Performance - Asset power failure | E.g. frequent power supply failure caused high spill frequency
Performance - Pump failure / issue | Spill frequency primarily caused by pump failure / premature spills; e.g. pumping station struggles to maintain PFF & review of rising main design required
Performance - Other maintenance / capital works (e.g. jetting) | Spill frequency primarily caused by works; e.g. jetting
Performance - Not designed to meet Bathing / Shellfish Water directive | Spill frequency threshold reached because asset not yet designed to meet BW or SFW requirements
Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Spill frequency primarily caused by inappropriate asset/configuration; e.g. inlet design causing premature spills & requires further investigation
Data collection - EDM non-representative location | E.g. Records multiple discharge points & cannot distinguish between the two. Requires relocation
Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | High spill frequency caused by exceptional weather events. Subsequent analysis of these data show adjusted spill frequency now not above SOAF threshold
Data collection - Tidal / river inundation | EDM spill frequency data quality affected by tidal or river inundation; e.g. tidal cycle causes levels to reverse flows in outfall pipe
Data collection - Poor quality (e.g. logger calibration / sensor issues) | E.g. logger calibration / sensor issues
Not asset maintenance - hydraulic capacity | Spill frequency primarily caused by hydraulic capacity issue rather than something that can be fixed operationally
Spill Frequency - Action taken / planned - Status & Timeframe | (Column U)
- Indicate whether action has already been taken / is planned to be taken, or whether there is an ongoing investigation to identify the appropriate action
- Which month this activity was completed / is planned
- Category must be selected when spill frequency exceeds SOAF threshold (using column P + data from previous years)
- See the more detailed User Guide (Word format) for table of definitions (page 11)
Drop-down options Column U:
Scheduled | Appropriate operational action to address spill frequency is planned
Resolved - January | Appropriate operational action has already been taken & issue affecting spill frequency resolved
Resolved - Feburary | As above
Resolved - March | As above
Resolved - April | As above
Resolved - May | As above
Resolved - June | As above
Resolved - July | As above
Resolved - August | As above
Resolved - September | As above
Resolved - October | As above
Resolved - November | As above
Resolved - December | As above
N/A - Ongoing investigation | Appropriate operational action not yet identified
N/A - Hydraulic Capacity | Issue is due to hydraulic capacity and unable to be fixed operationally through asset maintenance programme
Spill Frequency - Planning review position | (Column V)
- Action taken to address spill performance through the planning framework
- Select primary reason only
- Category must be selected when spill frequency exceeds SOAF threshold (using column O + data from previous years)
- Follows SOAF for addressing high frequency discharges from storm overflows under the UWWTR (see Figure 1 in SOAF document, 2018)
- Stage 1 of the SOAF should be applied to all high spills as good practice, as part of the initial investigation to understand whether spills were due to exceptional weather events, asset performance or hydraulic capacity. Stage 1 is expected on a continual rolling basis independent of any WINEP drivers.
- Progressing further past stage 1 is expected when a WINEP driver exists. Progressing past stage 1 without a WINEP driver would be proactive but at WaSC discretion.
- See the more detailed User Guide (Word format) for table of definitions (page 12)
Drop-down options Column V:
SOAF N/A - Proposed SFTP (overflow previously improved) | Schemes previously improved via SOAF but now identified for Spill Frequency Trigger Permitting
Stage 1a: Confirmed "exceptional weather" issue | See SOAF definition
Stage 1b: Confirmed "asset maintenance" issue | See SOAF definition
Stage 1c: Confirmed "hydraulic issue" | If not “exceptional weather” or “asset maintenance”
U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | SOAF invesitgation ongoing at Stage 2/3
U_INV driver - Stage 4: Cost beneficial outcome not yet determined | In process of Cost Benefit Analysis (CBA) but no outcome at present
U_INV driver - Stage 4: No cost beneficial solution | CBA indicates costs are disproportionate to environmental benefit
U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP7 or Green Recovery | U_INV CBA indicates spill reduction scheme is cost beneficial and is on current WINEP or other planned improvement programme
U_IMP4 driver - Stage 4: Potential spill reduction scheme - Not yet on current WINEP/AMP7 or Green Recovery | U_INV CBA indicates a spill reduction scheme may be cost beneficial
N/A - Operational solution applied | Planning framework not required - spill frequency remedied through operational solution

## SWW - SO
EDM STORM OVERFLOW REGULATORY ANNUAL RETURN
Please send to email inbox: askED@environment-agency.gov.uk
Please name file using the following convention: "EDM Return WaSC period.xls" .
For example if Severn Trent Water had a bathing water return for 2021 it would be "EDM Return Severn Trent Water Bathing Season 2021.xls"
For example if Wessex Water had a storm overflow annual return for 2021 it would be "EDM Return Wessex Water Storm Overflow Annual 2021.xls"
For example if Southern Water had an emergency overflow annual return for 2021 it would be "EDM Return Southern Water Emergency Overflow Annual 2021.xls"
Water Company Name | Site Name (EA Consents Database) | Site Name (WaSC operational) [optional] | EA Permit Reference (EA Consents Database) | WaSC Supplementary Permit Ref. [optional] | Activity Reference on Permit (if >1 discharge on permit) | Storm Discharge Asset Type | Outlet Discharge NGR (EA Consents Database) | WFD Waterbody ID (Cycle 2) (discharge outlet) | WFD Waterbody Catchment Name (Cycle 2) (discharge outlet) | Receiving Water / Environment (common name) (EA Consents Database) | Shellfish Water (only populate for storm overflow with a Shellfish Water EDM requirement) | Bathing Water (only populate for storm overflow with a Bathing Water EDM requirement) | Initial EDM Commission Date | Total Duration (hrs) all spills prior to processing through 12-24h count method | Counted spills using 12-24h count method | EDM Operation - % of reporting period EDM operational | EDM Operation - Reporting % - Primary Reason <90% | EDM Operation - Action taken / planned - Status & timeframe | High Spill Frequency - Operational Review - Primary Reason | High Spill Frequency - Action taken / planned - Status & timeframe | High Spill Frequency - Environmental Enhancement - Planning Position (Hydraulic capacity)
South West Water | 11 HIGH STREET CSO | 11 HIGH STREET_CSO_HATHERLEIGH | 201777 | 201777 | A1 | SO on sewer network | SS 5405 0422 | GB108050008220 | Lower River Lew (Torridge) | RIVER LEW |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | DUNNING WALK COMBINED SEWER OVERFLO | 12 DUNNINGS WALK_CSO_TEIGNMOUTH | 201684 | 201684 | A1 | SO on sewer network | SX 9315 7402 | 22 | #N/A | BITTEN BROOK (S) |  |  | Commissioned in 2018 - full year data expected | 0.83 | 5 | 97
South West Water | 121A ST. KATHERINES ROAD CSO | 121a ST KATHERINES RD_CSO_EXETER | 201904 | 201904 | A1 | SO on sewer network | SX 9419 9387 | GB108045009050 | North Brook (East Devon) | MINCINGLAKE STREAM | Exe |  | Commissioned in 2017 - full year data expected | 33.31 | 14 | 100
South West Water | BURNTHOUSE LANE CSO | 127 BURNTHOUSE LANE_CSO_EXETER | 202223 | 202223 | A1 | SO on sewer network | SX 9429 9124 | GB108045009050 | North Brook (East Devon) | NORTHBROOK VIA SWS | Exe |  | Commissioned in 2017 - full year data expected | 0.86 | 4 | 100
South West Water | 14 CLIFTON ROAD CSO | 14 CLIFTON RD_CSO_EXETER | 201920 | 201920 | A1 | SO on sewer network | SX 9223 9188 | GB108045009040 | Exe (Creedy to Estuary) | RIVER EXE VIA SWS | Exe |  | Commissioned in 2017 - full year data expected | 0 | 0 | 100
South West Water | 15 HAMLIN LANE CSO | 15 HAMLIN LN_CSO_EXETER | 201905 | 201905 | A1 | SO on sewer network | SX 9417 9341 | GB108045009050 | North Brook (East Devon) | NORTH BROOK | Exe |  | Commissioned in 2017 - full year data expected | 0 | 0 | 16 | comms failure / issue | N/A - Ongoing investigation
South West Water | BITTON PARK ROAD CSO | 153 BITTON PARK ROAD_CSO_TEIGNMOUTH | 203345 | 203345 | A1 | SO on sewer network | SX 9327 7295 | 22 | #N/A | TEIGN ESTUARY(E) | Teign |  | Commissioned pre-2016 - full year data expected | 0.52 | 3 | 82 | Sensor failure / issue | Resolved - August
South West Water | BITTON PARK ROAD JCT 2ND AVENUE CSO | 155 BITTON PARK ROAD_CSO_TEIGNMOUTH | 203205 | 203205 | A1 | SO on sewer network | SX 9328 7295 | 22 | #N/A | TEIGN ESTUARY(E) | Teign |  | Commissioned pre-2016 - full year data expected | 2.04 | 3 | 59 | Sensor failure / issue | Resolved - November
South West Water | 178 BEAUMONT ROAD CSO | 178 BEAUMONT ROAD_CSO_PLYMOUTH | 301789 | 301789 | A1 | SO on sewer network | SX 5015 5478 | 73 | #N/A | RIVER PLYM VIA SWS (ESTUARINE) |  |  | Commissioned in 2018 - full year data expected | 33.69 | 48 | 100
South West Water | JEPHSON ROAD CSO | 1A JEPHSON RD_CSO_PLYMOUTH | 301739 | 301739 | A1 | SO on sewer network | SX 5015 5478 | 73 | #N/A | RIVER PLYM VIA SWS (ESTUARINE) |  |  | Commissioned in 2018 - full year data expected | 15.98 | 17 | 74 | Sensor failure / issue | Resolved - January
South West Water | 2 BICKHAM PARK ROAD CSO | 2 BICKHAM PARK RD_CSO_PLYMOUTH | 301747 | 301747 | A1 | SO on sewer network | SX 4664 5492 | 73 | #N/A | PENNYCOMEQUICK STREAM VIA SWS |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 59 | Sensor failure / issue | Resolved - October
South West Water | 2 DRYDEN ROAD CSO | 2 DRYDEN RD_CSO_EXETER | 201910 | 201910 | A1 | SO on sewer network | SX 9430 9124 | GB108045009050 | North Brook (East Devon) | NORTH BROOK VIA SWS | Exe |  | Commissioned in 2017 - full year data expected | 0 | 0 | 100
South West Water | LOWER AVENUE CSO | 2 LOWER AVENUE_CSO_EXETER | 201912 | 201912 | A1 | SO on sewer network | SX 9479 9229 | GB108045009050 | North Brook (East Devon) | NORTH BROOK VIA SWS | Exe |  | Commissioned in 2018 - full year data expected | 0 | 0 | 100
South West Water | THE COLLEGE IDE CSO | 2 THE COLLEGE_CSO_IDE | 203624 | 203624 | A1 | SO on sewer network | SX 9001 9060 | GB108045009020 | Alphin Brook | FORDLAND BROOK | Exe |  | Commissioned in 2018 - full year data expected | 10.37 | 8 | 100
South West Water | 21 LOWER TOWN CSO | 21 LOWER TOWN_CSO_SAMPFORD PEVERELL | 201838 | 201838 | A1 | SO on sewer network | ST 0328 1423 | GB108045015020 | Spratford Stream | TRIBUTARY OF SPRATFORD STREAM |  |  | Commissioned in 2018 - full year data expected | 1.4 | 8 | 100
South West Water | 21 WONFORD STREET CSO | 21 WONFORD ST_CSO_EXETER | 201909 | 201909 | A1 | SO on sewer network | SX 9429 9124 | GB108045009050 | North Brook (East Devon) | NORTHBROOK VIA SWS | Exe |  | Commissioned in 2018 - full year data expected | 0 | 0 | 100
South West Water | 23 KING EDWARD STREET CSO | 23 KING EDWARD ST_CSO_EXETER | 201930 | 201930 | A1 | SO on sewer network | SX 9109 9380 | GB108045009040 | Exe (Creedy to Estuary) | RIVER EXE VIA SWS | Exe |  | Commissioned in 2018 - full year data expected | 241.67 | 14 | 100
South West Water | 3 ST PETERS CLOSE CSO | 23 ST. PETER CLOSE_CSO_PLYMOUTH | 301768 | 301768 | A1 | SO on sewer network | SX 5475 5558 | 73 | #N/A | LONG BROOK VIA SWS |  | PLYMOUTH HOE (EAST) | Commissioned in 2017 - full year data expected | 258.05 | 83 | 100
South West Water | CSO AT NORTH PARADE | 24 NORTH PARADE_CSO_FALMOUTH | 303011 | 303011 | A1 | SO on sewer network | SW 7989 3392 | 402 | #N/A | PENRYN RIVER(E) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 33.55 | 34 | 100
South West Water | TEMPLERS ROAD CSO | 25 TEMPLERS RD_CSO_NEWTON ABBOT | 202245 | 202245 | A1 | SO on sewer network | SX 8672 7169 | 22 | #N/A | RIVER LEMON VIA SWS | Teign |  | Commissioned in 2018 - full year data expected | 0 | 0 | 98
South West Water | 27 OAKLEA COMBINED SEWER OVEFLOW | 27 OAKLEA_CSO_HONITON | 201850 | 201850 | A1 | SO on sewer network | ST 1577 0070 | GB108045009180 | Middle River Otter | THE GISSAGE |  |  | Commissioned in 2019 - full year data expected | 9.13 | 12 | 95
South West Water | 28 CLIFTON ROAD CSO | 28 CLIFTON RD_CSO_EXETER | EPRDB3293NC | EPR/DB3293NC | A1 | SO on sewer network | SX 9224 9188 | GB108045009040 | Exe (Creedy to Estuary) | RIVER EXE VIA SWS | Exe |  | Commissioned in 2017 - full year data expected | 0.14 | 1 | 100
South West Water | 28 FINCH CLOSE CSO | 28 FINCH CLOSE_CSO_PLYMOUTH | 301785 | 301785 | A1 | SO on sewer network | SX 5058 5587 | 73 | #N/A | TRIB OF RIVER PLYM VIA SWS |  |  | Commissioned in 2018 - full year data expected | 0.61 | 1 | 100
South West Water | 31 FORE STREET CSO | 31 FORE STREET_CSO_TOTNES | 201955 | 201955 | A1 | SO on sewer network | SX 8057 6024 | 23 | #N/A | TRIB OF R.DART(E) VIA SW SEWER | Dart |  | Commissioned in 2019 - full year data expected | 23.23 | 36 | 90
South West Water | 34 CLIFTON ROAD CSO | 34 CLIFTON RD_CSO_EXETER | 201917 | 201917 | A1 | SO on sewer network | SX 9224 9189 | GB108045009040 | Exe (Creedy to Estuary) | RIVER EXE VIA SWS | Exe |  | Commissioned in 2017 - full year data expected | 0.13 | 1 | 100
South West Water | 39 ST MICHAELS COMBINED SEWER OF | 39 ST MICHAELS ROAD_CSO_PONSONOOTH | 301808 | 301808 | A1 | SO on sewer network | SW 7608 3769 | GB108048001140 | Kennal | RIVER KENNALL | Fal Estuary |  | Commissioned in 2019 - full year data expected | 1159.06 | 102 | 100
South West Water | OPP 44 CARMARTHEN ROAD CSO | 44 CARMARTHEN RD_CSO_PLYMOUTH | 301738 | 301738 | A1 | SO on sewer network | SX 5016 5478 | 73 | #N/A | RIVER PLYM (E) |  | PLYMOUTH HOE (EAST) | Commissioned in 2017 - full year data expected | 4.69 | 14 | 100
South West Water | 45 CRAVEN AVENUE CSO | 45 CRAVEN AVENUE_CSO_PLYMOUTH | 301771 | 301771 | A1 | SO on sewer network | SX 5015 5478 | 73 | #N/A | RIVER PLYM VIA SWS (ESTUARINE) |  |  | Commissioned in 2018 - full year data expected | 1.19 | 1 | 100
South West Water | 49 EXETER ROAD CSO | 49 EXETER ROAD_CSO_DAWLISH | 200826 | 200826 | A1 | SO on sewer network | SX 9679 7705 | 20 | #N/A | ENGLISH CHANNEL VIA SWS |  |  | Commissioned in 2019 - full year data expected | 5.22 | 11 | 91
South West Water | SANDRINGHAM PARK CSO | 51 SANDRINGHAM RD_CSO_NEWTON ABBOT | 203340 | 203340 | A1 | SO on sewer network | SX 8720 7114 | GB108046005350 | Aller Brook (Teign) - Lower | ALLER BROOK(S) | Teign |  | Commissioned pre-2016 - full year data expected | 30.03 | 13 | 100
South West Water | FARRINGDON ROAD CSO | 5 FARINGDON ROAD_CSO_PLYMOUTH | 301732 | 301732 | A1 | SO on sewer network | SX 5015 5478 | 73 | #N/A | RIVER PLYM VIA SWS (ESTUARINE) |  | PLYMOUTH HOE (EAST) | Commissioned in 2016 - full year data expected | 16 | 19 | 100
South West Water | BARTON DRIVE CSO | 59 BARTON DRIVE_CSO_NEWTON ABBOT | 203381 | 203381 | A1 | SO on sewer network | SX 8494 7126 | GB108046008450 | Lemon | TRIBUTARY OF RIVER LEMON(S) | Teign |  | Commissioned pre-2016 - full year data expected | 457.29 | 70 | 100
South West Water | 59 BRETONSIDE CSO | 59 BRETONSIDE_CSO_PLYMOUTH | 301752 | 301752 | A1 | SO on sewer network | SX 4839 5442 | 73 | #N/A | SUTTON HARBOUR VIA SWS (ESTU.) |  | PLYMOUTH HOE (EAST) | Commissioned in 2017 - full year data expected | 250.43 | 64 | 100
South West Water | 5A HIGH STREET CSO | 5A HIGH STREET_CSO_HATHERLEIGH | 201776 | 201776 | A1 | SO on sewer network | SS 5405 0422 | GB108050008220 | Lower River Lew (Torridge) | RIVER LEW VIA SWS |  |  | Commissioned pre-2016 - full year data expected | 1.37 | 10 | 100
South West Water | 78 BEAUMONT ROAD CSO | 78 BEAUMONT ROAD_CSO_PLYMOUTH | 301782 | 301782 | A1 | SO on sewer network | SX 5015 5478 | 73 | #N/A | RIVER PLYM VIA SWS (ESTUARINE) |  |  | Commissioned in 2017 - full year data expected | 7.66 | 26 | 100
South West Water | 8 HIGH STREET CSO | 8 HIGH STREET_CSO_HATHERLEIGH | 201775 | 201775 | A1 | SO on sewer network | SS 5405 0422 | GB108050008220 | Lower River Lew (Torridge) | RIVER LEW VIA SWS |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | A382 BYPASS VERGE CSO | A382 BYPASS VERGE_CSO_BOVEY TRACEY | 201807 | 201807 | A1 | SO on sewer network | SX 8198 7708 | GB108046008470 | Lower Bovey | TRIB OF RIVER BOVEY VIA SWS | Teign |  | Commissioned in 2018 - full year data expected | 1.83 | 3 | 100
South West Water | O/S 11 KINGSTEIGNTON ROAD CSO | ABBOTSBURY RD_CSO_NEWTON ABBOT | 203092 | 203092 | A1 | SO on sewer network | SX 8634 7167 | 22 | #N/A | THE ALLER BROOK (S) | Teign |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | ABBOTSHAM WWTW | ABBOTSHAM STW_SO_ABBOTSHAM | DRA 459 | DRA 459 | A2 | Inlet SO at WwTW | SS 4280 2678 | GB108050014500 | Kenwith Stream | KENWITH STREAM |  |  | Commissioned in 2017 - full year data expected | 1148.81 | 332 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: Cost beneficial outcome not yet determined
South West Water | ADIT LANE CSO | ADIT LANE_CSO_SALTASH | 302582 | 302582 | A1 | SO on sewer network | SX 4256 5941 | 71 | #N/A | TRIBUTARY OF SALTMILL CREEK(S) | Tamar |  | Commissioned pre-2016 - full year data expected | 32.28 | 18 | 100
South West Water | KEYBERRY RD NO.5 CSO | ADJ NO 5 KEYBERRY RD_CSO_NEWTON ABBOT | 203101 | 203101 | A1 | SO on sewer network | SX 8706 7050 | GB108046005350 | Aller Brook (Teign) - Lower | SEWER TO ALLER BROOK (S) | Teign |  | Commissioned pre-2016 - full year data expected | 51.66 | 17 | 100
South West Water | ALLER BRAKE ROAD CSO | ALLER BRAKE RD_CSO_NEWTON ABBOT | 203093 | 203093 | A1 | SO on sewer network | SX 8740 6988 | GB108046005350 | Aller Brook (Teign) - Lower | SURFACE WATER SEWER (S) | Teign |  | Commissioned pre-2016 - full year data expected | 2.95 | 8 | 100
South West Water | ALLOTMENT CSO | ALLOTMENT OPP BICKHAM PK RD_CSO_PLYMOUTH | 301781 | 301781/CS/01 | A1 | SO on sewer network | SX 4622 5441 | 73 | #N/A | STONEHOUSE CREEK (E) |  |  | EDM to be installed by December 2023
South West Water | ANCHORWOOD PS | ANCHORWOOD SPS_PSCSOEO_BARNSTAPLE | 203281 | 203281 | A1 | Storm discharge at pumping station | SS 5557 3301 | 198 | #N/A | RIVER TAW ESTUARY(E) | Taw/Torridge |  | Commissioned pre-2016 - full year data expected | 45.8 | 16 | 82 | Sensor failure / issue | Resolved - September
South West Water | ANTONY STW (INLET TO WORKS) SSO | ANTONY S T SEPTNK_SO_ANTONY | NRA-SW-1004 | NRA-SW-1004 | A2 | Inlet SO at WwTW | SX 3984 5480 | 72 | #N/A | RIVER LYNHER ESTUARY | Lynher |  | Commissioned in 2019 - full year data expected | 468.62 | 101 | 100
South West Water | APPLEDORE PS | APPLEDORE SPS_PSCSOEO_APPLEDORE | 203123 | 203123 | A1 | Storm discharge at pumping station | SS 4649 3077 | 199 | #N/A | RIVER TORRIDGE ESTUARY (E) | Taw/Torridge | INSTOW BEACH | Commissioned pre-2016 - full year data expected | 0.97 | 1 | 100
South West Water | APPLETREE CSO | APPLETREE_CSO_KINGSTON | 201761 | 201761 | A1 | SO on sewer network | SX 6370 4768 | 266 | #N/A | TRIB OF THE ENGLISH CHANNEL |  |  | Commissioned in 2020 - full year data expected | 15.22 | 20 | 50 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | ARGYLL ROAD PUMPING STATION | ARGYLL ROAD SPS_PSCSOEO_EXETER | 203045 | 203045 | A1 | Storm discharge at pumping station | SX 9212 9498 | GB108045009040 | Exe (Creedy to Estuary) | TRIBUTARY OF DURYARD STREAM | Exe |  | Commissioned in 2016 - full year data expected | 0 | 0 | 100
South West Water | ARNOLDS POINT PUMPING STATION | ARNOLDS POINT SPS_PSCSOEO_PLYMOUTH | 301988 | 301988 | A1 | Storm discharge at pumping station | SX 5039 5533 | 73 | #N/A | RIVER PLYM VIA SWS (ESTUARINE) |  |  | Commissioned in 2016 - full year data expected | 15.46 | 3 | 100
South West Water | ASH GROVE CSO | ASH GROVE_CSO_EXMOUTH | 200127/CS/01 | 200127/CS/01 | A1 | SO on sewer network | SY 0003 8307 | 19 | #N/A | A TRIBUTARY OF THE EXE ESTUARY | Exe |  | Commissioned pre-2016 - full year data expected | 26.86 | 22 | 92
South West Water | BARNSTAPLE (ASHFORD) STW | ASHFORD STW_SSO_BARNSTAPLE | 2491 | 2491 | A2 | Storm tank at WwTW | SS 5325 3406 | 198 | #N/A | RIVER TAW ESTUARY | Taw/Torridge |  | Commissioned pre-2016 - full year data expected | 1694.6 | 112 | 100
South West Water | ASHPRINGTON WWTW | ASHPRINGTON STW_SO_ASHPRINGTON | NRA-SW-3983 | NRA-SW-3983 | A2 | Inlet SO at WwTW | SX 8148 5636 | 23 | #N/A | RIVER HARBOURNE (ESTUARINE) |  |  | Commissioned in 2016 - full year data expected | 88.93 | 69 | 100
South West Water | ASHPRINGTON WWTW | ASHPRINGTON STW_SSO_ASHPRINGTON | NRA-SW-3983 | NRA-SW-3983 | A3 | Storm tank at WwTW | SX 8148 5636 | 23 | #N/A | RIVER HARBOURNE (ESTUARINE) | Dart |  | Commissioned in 2016 - full year data expected | 1116.34 | 97 | 100
South West Water | ASHREIGNY WWTW CSO | ASHREIGNEY STW_SO_ASHREIGNEY | NRA-SW-1006 | NRA-SW-1006 | A2 | Inlet SO at WwTW | SS 6207 1383 | GB108050014310 | Mully Brook | TRIB OF MULLY BROOK |  |  | EDM to be installed by December 2023
South West Water | ASHWATER STW | ASHWATER STW_SO_ASHWATER | NRA-SW-6738 | NRA-SW-6738 | A2 | Inlet SO at WwTW | SX 3929 9530 | GB108047008040 | Carey | (S) RIVER CAREY |  |  | EDM to be installed by December 2023
South West Water | ATHERINGTON WWTW CSO | ATHERINGTON STW_SO_ATHERINGTON | NRA-SW-1008 | NRA-SW-1008 | A2 | Inlet SO at WwTW | SS 5933 2312 | GB108050014530 | Taw (River Mole to Estuary) | TRIB OF CHANTRY STREAM |  |  | EDM to be installed by December 2023
South West Water | AVETON GIFFORD STW | AVETON GIFFORD STW_SSO_AVETON GIFFORD | 202403 | 202403 | A2 | Storm tank at WwTW | SX 6910 4729 | 24 | #N/A | RIVER AVON ESTUARY(E) | Avon | BANTHAM BEACH | Commissioned pre-2016 - full year data expected | 11.3 | 7 | 100
South West Water | AWLISCOMBE PUMPING STATION | AWLISCOMBE SPST_PSCSOEO_AWLISCOMBE | 201638 | 201638 | A1 | Storm discharge at pumping station | ST 1364 0112 | GB108045009190 | Wolf (Otter) | TRIB OF RIVER WOLF |  |  | Commissioned in 2017 - full year data expected | 417.78 | 37 | 100
South West Water | AXMOUTH PSCSO/EO | AXMOUTH SPST_PSCSOEO_AXMOUTH | 201605 | 201605/PC/01 | A1 | Storm discharge at pumping station | SY 2553 9107 | 17 | #N/A | RIVER AXE (S) |  | SEATON BEACH | Commissioned pre-2016 - full year data expected | 160.56 | 22 | 100
South West Water | AYLIFFE'S BRIDGE CSO | AYLIFFE'S FIELD_CSO_BOVEY TRACEY | 201806 | 201806 | A1 | SO on sewer network | SX 8168 7811 | GB108046008470 | Lower Bovey | RIVER BOVEY | Teign |  | Commissioned in 2018 - full year data expected | 176.64 | 46 | 100
South West Water | BEACH ROAD PSCSO/EO | BABBACOMBE(1) SPS_PSCSOEO_BABBACOMBE | 201609 | 201609/PC/01 | A1 | Storm discharge at pumping station | SX 9306 6553 | 409 | #N/A | ENGLISH CHANNEL (C) |  | BABBACOMBE BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | BEACH ROAD (MIDDLE) | BABBACOMBE(2) SPS_PSCSOEO_BABBACOMBE | 201524 | 201524/PC/01 | A1 | Storm discharge at pumping station | SX 9306 6553 | 409 | #N/A | ENGLISH CHANNEL (C) |  | BABBACOMBE BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | BEACH ROAD (UPPER) | BABBACOMBE(3) SPS_PSCSOEO_BABBACOMBE | 201525 | 201525/PC/01 | A1 | Storm discharge at pumping station | SX 9306 6553 | 409 | #N/A | ENGLISH CHANNEL (C) |  | BABBACOMBE BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | BAMPTON WWTW | BAMPTON STW_SSO_BAMPTON | SWWA 42 | SWWA 42 | A2 | Storm tank at WwTW | SS 9541 2179 | GB108045015070 | Lower Batherm | RIVER BATHERM |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 100
South West Water | BANK STREET CSO | BANK STREET_CSO_NEWTON ABBOT | 201958 | 201958 | A1 | SO on sewer network | SX 8577 7135 | GB108046008450 | Lemon | TRIB O RIVER LEMON VIA SW SEWR | Teign |  | Commissioned in 2018 - full year data expected | 0 | 0 | 89 | Comms failure / issue | Resolved - April
South West Water | BARBICAN (SUTTON HARBOUR) TANKS | BARBICAN TANKS_CSOEO_PLYMOUTH | 300821 | 300821 | A1 | SO on sewer network | SX 4834 5367 | 73 | #N/A | PLYMOUTH SOUND (E) |  | PLYMOUTH HOE (EAST) | Commissioned pre-2016 - full year data expected | 20.21 | 4 | 100
South West Water | BARN PARK ROAD CSO | BARN PARK ROAD_CSO_PLYMOUTH | 301755 | 301755 | A1 | SO on sewer network | SX 4664 6492 | 71 | #N/A | PENNYCOMEQUICK STREAM VIA SWS |  |  | Commissioned in 2017 - full year data expected | 6.13 | 18 | 100
South West Water | BARRIS CSO | BARRIS VIEW_CSO_LAPFORD | 201847 | 201847/CS/01 | A1 | SO on sewer network | SS 7269 0804 | GB108050014640 | Lower River Yeo (Lapford) | RIVER YEO (S) |  |  | EDM to be installed by December 2023
South West Water | BARTON DRIVE CSO | BARTON DR_CSO_NEWTON ABBOT | 201752 | 201752 | A1 | SO on sewer network | SX 8502 7116 | GB108046008450 | Lemon | TRIB OF RIVER LEMON VIA SWS |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 66 | Comms failure / issue | Resolved - August
South West Water | BARTON HILL ROAD CSO | BARTON HILL RD_CSO_TORQUAY | 201940 | 201940 | A1 | SO on sewer network | SX 9008 6623 | GB108046005330 | Aller Brook (Teign) - Upper | ALLER BROOK VIA SW SEWER |  |  | Commissioned in 2017 - full year data expected | 29.23 | 34 | 100
South West Water | BARTON HILL/BRUNSWICK CSO | BARTON HILL/BRUNSWICK PL_CSO_DAWLISH | 200823 | 200823/CS/01 | A1 | SO on sewer network | SX 9592 7667 | GB108045008910 | Dawlish Water | DAWLISH WATER (S) |  | DAWLISH (TOWN) BEACH | Commissioned pre-2016 - full year data expected | 16.05 | 21 | 87 | Comms failure / issue | Resolved - June
South West Water | LYNTON/LYNMOUTH SEWERAGE | BASKET SHOP SPS_PSCSOEO_LYNMOUTH | 004517/PC/01 | 004517/PC/01 | A1 | Storm discharge at pumping station | SS 7236 4984 | 237 | #N/A | LYNMOUTH BAY (E) |  | LYNMOUTH BEACH | Commissioned pre-2016 - full year data expected | 153.76 | 42 | 94
South West Water | BATSON GREEN PUMPING STATION | BATSON SPS_PSCSOEO_SALCOMBE | NRA-SW-7652/PC/1 | NRA-SW-7652 | A1 | Storm discharge at pumping station | SX 7350 3971 | 69 | #N/A | BASTON CREEK (ESTUARINE) |  |  | Commissioned in 2016 - full year data expected | 96.91 | 28 | 100
South West Water | BATTS LANE COMBINED SEWER OVERFLOW | BATTS LANE_CSO_OTTERY ST. MARY | 201383 | 201383 | A1 | SO on sewer network | SY 0996 9545 | GB108045009170 | Lower River Otter | TRIBUTARY OF RIVER OTTER |  |  | Commissioned in 2019 - full year data expected | 4 | 14 | 100
South West Water | BEACH ROAD | BEACH RD_CSO_TORQUAY | 201939 | 201939/CS/01 | A1 | SO on sewer network | SX 9319 6547 | 409 | #N/A | ENGLISH CHANNEL (C) |  | BABBACOMBE BEACH | Commissioned pre-2016 - full year data expected | 1.6 | 2 | 100
South West Water | BEACON HILL | BEACON HILL_CSO_TORQUAY | 200222 | 200222 | A1 | SO on sewer network | SX 9183 6322 | 429 | #N/A | NEW HARBOUR TORQUAY |  | BEACON COVE BEACH | Commissioned pre-2016 - full year data expected | 3.72 | 13 | 74 | Sensor failure / issue | Resolved - October
South West Water | BEACON SIDE PSCSO/EO | BEACONSIDE SPS_PSCSOEO_FOXHOLE | 301616 | 301616/PC/01 | A1 | Storm discharge at pumping station | SW 9614 5472 | GB108048001350 | Gwindra Stream | STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | BEALS MILL NO 1 CSO | BEALS MILL NO 1_CSO_TREBURLEY | 301889 | 301889 | A1 | SO on sewer network | SX 3596 7707 | GB108047007890 | Lower River Inny | RIVER INNY |  |  | Commissioned in 2018 - full year data expected | 588.28 | 93 | 40 | Comms failure / issue | Resolved - November | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP7 or Green Recovery
South West Water | BEALS MILL NO 2 CSO | BEALS MILL NO 2_CSO_TREBURLEY | 301890 | 301890 | A1 | SO on sewer network | SX 3596 7707 | GB108047007890 | Lower River Inny | RIVER INNY |  |  | Commissioned in 2018 - full year data expected | 5619.88 | 361 | 99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP7 or Green Recovery
South West Water | BEALS MILL PUMPING STATION | BEALS MILL SPS_PSCSOEO_BEALS MILL | 301644 | 301644 | A1 | Storm discharge at pumping station | SX 3589 7703 | GB108047007890 | Lower River Inny | A TRIBUTARY OF RIVER INNY |  |  | Commissioned in 2020 - full year data expected | 3543.63 | 163 | 100
South West Water | BEALS MILL WWTW | BEALS MILL STW_SO_REZARE | SWWA 880 | SWWA 880 | A2 | Inlet SO at WwTW | SX 3596 7707 | GB108047007890 | Lower River Inny | RIVER INNY |  |  | Commissioned in 2019 - full year data expected | 4.15 | 7 | 100
South West Water | BEDFORD BRIDGE CSO | BEDFORD BRIDGE_CSO_HORRABRIDGE | 300964 | 300964 | A1 | SO on sewer network | SX 5029 7037 | GB108047007870 | Walkham | RIVER WALKHAM |  |  | Commissioned in 2019 - full year data expected | 1297.89 | 114 | 100
South West Water | BERE ALSTON STW | BERE ALSTON STW_SO_BERE ALSTON | NRA-SW-3792 | NRA-SW-3792 | A2 | Inlet SO at WwTW | SX 4271 6630 | 71 | #N/A | TIDAL RIVER TAMAR |  |  | Commissioned in 2018 - full year data expected | 3251.87 | 174 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP7 or Green Recovery
South West Water | BERE ALSTON STW | BERE ALSTON STW_SSO_BERE ALSTON | NRA-SW-3791 | NRA-SW-3791 | A3 | Storm tank at WwTW | SX 4271 6630 | 71 | #N/A | (E)TIDAL RIVER TAMAR |  |  | Commissioned in 2018 - full year data expected | 2958.49 | 179 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP7 or Green Recovery
South West Water | BERE ALSTON COMBINED SEWER OVERFLOW | BERE ALSTON_CSO_BERE ALSTON | 301824 | 301824 | A1 | SO on sewer network | SX 4463 6681 | 71 | #N/A | TRIB OF RIVER TAMAR VIA SWS |  |  | Commissioned in 2019 - full year data expected | 23.71 | 43 | 100
South West Water | BERE FERRERS PUMPING STATION | BERE FERRERS SPST_PSCSOEO_BERE FERRERS | NRA-SW-3786 | NRA-SW-3786 | A1 | Storm discharge at pumping station | SX 4611 6332 | 71 | #N/A | RIVER TAVY (ESTUARINE) |  |  | Commissioned in 2018 - full year data expected | 285.81 | 90 | 100
South West Water | BERRY HEAD ROAD CSO | BERRY HEAD_CSO_BRIXHAM | 202705 | 202705 | A1 | SO on sewer network | SX 9327 5667 | 429 | #N/A | TORBAY(C) | Brixham | SHOALSTONE BEACH | Commissioned pre-2016 - full year data expected | 11.3 | 18 | 100
South West Water | BERRYNARBOR PS CSO | BERRYNARBOR SPST_PSCSOEO_BERRYNARBOR | 202185/CS/01 | 202185/CS/01 | A1 | Storm discharge at pumping station | SS 5580 4665 | GB108051020470 | Sterridge | UNNAMED STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | BESSOM BRIDGE PUMPING STATION | BESSOM BRIDGE SPST_PSCSOEO_WIMBLEBALL | 202159 | 202159 | A1 | Storm discharge at pumping station | SS 9740 3187 | GB108045020900 | Upper River Haddeo | WIMBLEBALL LAKE |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 100
South West Water | BICKLEIGH WWTW | BICKLEIGH STW_SO_BICKLEIGH | SWWA 488 | SWWA 488 | A2 | Inlet SO at WwTW | SS 9401 0700 | GB108045015050 | Exe (Barle to Culm) | TRIB OF RIVER EXE |  |  | Commissioned in 2020 - full year data expected | 1345.34 | 123 | 100
South West Water | BIDEFORD FINE SCREENING | BIDEFORD FSCN SPST_PSCSOEO_BIDEFORD | 203116 | 203116 | A1 | Storm discharge at pumping station | SS 4566 2737 | 199 | #N/A | RIVER TORRIDGE (E) | Taw/Torridge | INSTOW BEACH | Commissioned pre-2016 - full year data expected | 44.05 | 43 | 100
South West Water | BIGBURY & CHALLABOROUGH STW | BIGBURY CHALLABOROUGH STW_SO_BIGBURY BAY | 202186/CS/01 | 202186/CS/01 | A2 | Inlet SO at WwTW | SX 6483 4442 | 266 | #N/A | BIGBURY BAY(C) |  | BIGBURY-ON-SEA (NORTH) BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | BILLACOMBE PUMPING STATION | BILLACOMBE_PSCSOEO_PLYMOUTH | 032897/PC/01 | 32897 | A1 | Storm discharge at pumping station | SX 5062 5387 | 73 | #N/A | POMPHLETT CREEK (ESTUARINE) |  | PLYMOUTH HOE (EAST) | Commissioned pre-2016 - full year data expected | 43.52 | 35 | 100
South West Water | BISHOP MEAD COMBINED SEWER OVERFLOW | BISHOPS MEAD_CSO_TAVISTOCK | 301883 | 301883 | A1 | SO on sewer network | SX 4827 7289 | GB108047007840 | Lower River Tavy | TIDDY BROOK |  |  | Commissioned in 2016 - full year data expected | 48.73 | 26 | 100
South West Water | BISHOPS TAWTON PUMPING STATION | BISHOPS TAWTON_PSCSOEO_BARNSTAPLE | 200204/PC/01 | 200204 | A1 | Storm discharge at pumping station | SS 5647 3020 | 198 | #N/A | RIVER VENN (ESTUARINE) | Taw/Torridge |  | Commissioned in 2016 - full year data expected | 37.1 | 22 | 100
South West Water | BISHOPSTEIGNTON PS | BISHOPSTEIGNTON SPS_PSCSOEO_BISHOPSTEIG | NRA-SW-2866 | NRA-SW-2866 | A1 | Storm discharge at pumping station | SX 9117 7275 | 22 | #N/A | TEIGN ESTUARY | Teign |  | Commissioned pre-2016 - full year data expected | #N/A | #N/A | 0 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | BITTON PARK ROAD JCT 2ND AVENUE CSO | BITTON PARK RD/SECOND AV_CSO_TEIGNMOUTH | 201683 | 201683 | A1 | SO on sewer network | SX 9328 7298 | 22 | #N/A | BITTON BROOK VIA SWS |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 100
South West Water | BLACK TORRINGTON WWTW | BLACK TORRINGTON STW_SO_BLACK TORRINGTON | 200364 | 200364 | A2 | Inlet SO at WwTW | SS 4694 0598 | GB108050013930 | Torridge (Combe Lake to Lew) | RIVER TORRIDGE (AND TRIB OF) |  |  | Commissioned in 2019 - full year data expected | 1144.31 | 124 | 100
South West Water | BLACKAWTON SEWAGE TREATMENT WORKS | BLACKAWTON STW_SSO_BLACKAWTON | NPSWQD006916 | NPSWQD006916 | A2 | Storm tank at WwTW | SX 8050 5043 | GB108046004930 | The Gara | BLACKAWTON STREAM |  |  | Commissioned in 2019 - full year data expected | 1117.46 | 91 | 100
South West Water | BLACKBROOK-CSO-PRINCETOWN | BLACKBROOK NORTH_CSO_PRINCETOWN | 201856 | 201856/CS/01 | A1 | SO on sewer network | SX 5909 7423 | GB108046008370 | Blackbrook River | BLACK BROOK RIVER (S) |  |  | EDM to be installed by December 2023
South West Water | BLACKWATER STW | BLACKWATER STW_SO_BLACKWATER | NRA-SW-7828 | NRA-SW-7828/SO/01 | A2 | Inlet SO at WwTW | SW 7400 4651 | GB108048001160 | Upper Carnon River | (S) RIVER CARNON | Fal Estuary |  | Commissioned in 2020 - full year data expected | 22.84 | 27 | 100
South West Water | BLOWING HOUSE LANE CSO | BLOWING HSE LN_CSO_BODMIN | 301825 | 301825 | A1 | SO on sewer network | SX 0557 6570 | GB108049000040 | St Lawrence Stream | ST LAWRENCE STREAM |  |  | Commissioned in 2019 - full year data expected | 1815.13 | 125 | 89 | Comms failure / issue | Resolved - April
South West Water | BOAT YARD PS CSO/EO | BOAT YARD SPS_PSCSOEO_MALPAS | 302829 | 302829 | A1 | Storm discharge at pumping station | SW 8457 4283 | 76 | #N/A | TRESILLIAN RIVER ESTUARY | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | BODINNICK COMBINED SEWER OVERFLOW | BODINNICK_CSO_FOWEY | 303432 | 303432 | A1 | SO on sewer network | SX 1291 5217 | 26 | #N/A | RIVER FOWEY ESTUARY | Fowey |  | Commissioned in 2017 - full year data expected | #N/A | #N/A | 0 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | BOJEWYAN PSCSO/EO | BOJEWYAN SPS_PSCSOEO_ST JUST | 301603 | 301603/PC/01 | A1 | Storm discharge at pumping station | SW 3905 3466 | 230 | #N/A | STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | BOLITHO ROAD CSO | BOLITHO RD_CSO_PENZANCE | NRA-SW-6340 | NRA-SW-6340 | A1 | SO on sewer network | SW 4637 3147 | 405 | #N/A | SURFACE WATER DRAIN TO CHYANDR |  | LONG ROCK | Commissioned pre-2016 - full year data expected | 212.29 | 90 | 100
South West Water | BOLTON STREET CSO | BOLTON STREET_CSO_BRIXHAM | 201010 | 201010/CS/01 | A1 | SO on sewer network | SX 9397 5458 | 409 | #N/A | ENGLISH CHANNEL(C) |  | ST.MARYS BAY BEACH | Commissioned pre-2016 - full year data expected | 65.46 | 48 | 100
South West Water | HEALTH CENTRE CAR PARK PSEO/CSO | BONE MILL SPS_PSCSOEO_LOOE | 300975 | 300975/PC/01 | A1 | Storm discharge at pumping station | SX 2543 5367 | 74 | #N/A | LOOE RIVER (HARBOUR) (E) |  | EAST LOOE BEACH | Commissioned pre-2016 - full year data expected | 435.89 | 109 | 75 | Comms failure / issue | Resolved - October | Performance - Infiltration | N/A - Ongoing investigation | N/A - Operational solution applied
South West Water | BONHAY PARK CSO | BONHAY PARK_CSO_EXETER | 202095 | 202095 | A1 | SO on sewer network | SX 9140 9231 | GB108045009040 | Exe (Creedy to Estuary) | RIVER EXE | Exe |  | Commissioned in 2017 - full year data expected | 20.5 | 7 | 100
South West Water | BONHAY ROAD CSO | BONHAY RD_CSO_STARCROSS | 202625 | 202625 | A1 | SO on sewer network | SX 9766 8184 | 20 | #N/A | TIDAL RIVER EXE(E) | Exe |  | Commissioned pre-2016 - full year data expected | 23.59 | 14 | 100
South West Water | BOOBERY ROAD COMBINED SEWER OVERFLO | BOOBERY RD_CSO_SAMPFORD PEVERELL | 201839 | 201839 | A1 | SO on sewer network | ST 0303 1437 | GB108045015020 | Spratford Stream | TRIB OF SPRATFORD STREAM |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 91
South West Water | BOSCASTLE HARBOUR PUMPING STATION | BOSCASTLE SPS_PSCSOEO_BOSCASTLE | 303079 | 303079 | A1 | Storm discharge at pumping station | SX 0940 9162 | GB610807680002 | Cornwall North | ATLANTIC OCEAN(C) |  |  | EDM to be installed by December 2023
South West Water | GEEVOR MINE PUMPING STATION | BOSCASWELL_PSCSOEO_PENZANCE | 303095 | 303095 | A1 | Storm discharge at pumping station | SW 3716 3491 | 230 | #N/A | ATLANTIC OCEAN COASTAL |  |  | Commissioned in 2018 - full year data expected | 99.54 | 26 | 100
South West Water | BOSORNE ROAD SEWER OVERFLOW | BOSORNE RD 1_CSOEO_ST JUST | 303091 | 303091 | A1 | SO on sewer network | SW 3550 3100 | 230 | #N/A | ATLANTIC / PORTH NANVEN STREAM |  |  | Commissioned in 2020 - full year data expected | 16.9 | 21 | 74 | Comms failure / issue | Resolved - April
South West Water | BOSSINEY BACK LANE PUMPING STATION | BOSSINEY BACK LANE_PSCSOEO_TINTAGEL | NPSWQD008115 | NPSWQD008115 | A1 | Storm discharge at pumping station | SX 0600 8932 | 234 | #N/A | ATLANTIC OCEAN |  |  | EDM to be installed by December 2023
South West Water | BOSVIGO LANE CSO | BOSVIGO LN_CSO_TRURO | 302673 | 302673 | A1 | SO on sewer network | SW 8161 4525 | GB108048002340 | Kenwyn | FRESHWATER(S) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 3.88 | 1 | 100
South West Water | BOTALLACK PUMPING STATION | BOTALLACK_PSCSOEO_TREGESEAL | 303093 | 303093 | A1 | Storm discharge at pumping station | SW 3615 3312 | 230 | #N/A | ATLANTIC OCEAN (C) |  |  | Commissioned in 2018 - full year data expected | 32.85 | 26 | 100
South West Water | LYNTON/LYNMOUTH | BOTTOM MEADOW_CSO_LYNTON | 004518/CS/01 | 004518/CS/01 | A1 | SO on sewer network | SS 7209 4929 | GB108051020600 | West Lyn River | LADY WELL STREAM (S) |  | LYNMOUTH BEACH | Commissioned pre-2016 - full year data expected | 1.04 | 2 | 100
South West Water | BOVEY BRIDGE CSO | BOVEY BRIDGE_CSO_BOVEY TRACEY | 201805 | 201805 | A1 | SO on sewer network | SX 8148 7826 | GB108046008470 | Lower Bovey | RIVER BOVEY | Teign |  | Commissioned in 2019 - full year data expected | 1.2 | 2 | 95
South West Water | WWTW AT BRADNINCH | BRADNINCH STW_SSO_BRADNINCH | SWWA 683 | SWWA 683 | A2 | Storm tank at WwTW | ST 0057 0331 | GB108045014970 | Lower Culm | RIVER CULM |  |  | Commissioned in 2018 - full year data expected | 1289.82 | 103 | 100
South West Water | BRANSCOMBE PSCSO/EO | BRANSCOMBE SPST_PSCSOEO_BRANSCOMBE | 201531 | 201531/PC/01 | A1 | Storm discharge at pumping station | SY 2076 8816 | 407 | #N/A | BRANSCOMBE (C) |  |  | EDM to be installed by December 2023
South West Water | BRANSCOMBE WWTW | BRANSCOMBE STW_SSO_BRANSCOMBE | 003101/FN/01 | 3101 | A2 | Storm tank at WwTW | SY 2059 8832 | GB108045008630 | Branscombe Stream | BRANSCOMBE STREAM |  |  | Commissioned in 2017 - full year data expected | 75.55 | 17 | 81 | Sensor failure / issue | Resolved - October
South West Water | BRAYFORD STW | BRAYFORD STW_SO_BRAYFORD | 202187/CS/01 | 202187/CS/01 | A2 | Inlet SO at WwTW | SS 6843 3444 | GB108050019950 | Bray (Source to Hole Water) | RIVER BRAY(S) |  |  | EDM to be installed by December 2023
South West Water | BREAGESIDE PUMPING STATION (PORTHLE | BREAGESIDE SPS_PSCSOEO_PORTHLEVEN | 300392/PC/01 | 300392/PC/01 | A1 | Storm discharge at pumping station | SW 6282 2561 | 269 | #N/A | MOUNTS BAY, ENGLISH CHANNEL |  | PORTHLEVEN SANDS | Commissioned pre-2016 - full year data expected | 13.22 | 4 | 94
South West Water | BRENT MILL CSO | BRENT MILL_CSO_SOUTH BRENT | 201720 | 201720 | A1 | SO on sewer network | SX 6973 5962 | GB108046004940 | Avon - Upper | RIVER AVON | Avon |  | Commissioned in 2018 - full year data expected | 52.77 | 26 | 85 | Comms failure / issue | Resolved - April
South West Water | PLAYING FIELDS CSO | BRIDESTOW_CSO_BRIDESTOW | 301828 | 301828/CS/01 | A1 | SO on sewer network | SX 5130 8943 | GB108047007770 | Lew (Tamar) | RIVER LYD (S) |  |  | EDM to be installed by December 2023
South West Water | BRIDESTOWE WWTW | BRIDESTOWE STW_SO_BRIDESTOWE | NRA-SW-3794 | NRA-SW-3794 | A2 | Inlet SO at WwTW | SX 5000 8926 | GB108047007770 | Lew (Tamar) | RIVER LEW |  |  | Commissioned in 2018 - full year data expected | 5169.63 | 293 | 100
South West Water | BRIDFORD WWTW | BRIDFORD STW_SO_TEIGN VALLEY | NRA-SW-6988 | NRA-SW-6988 | A2 | Inlet SO at WwTW | SX 8176 8610 | GB108046008540 | Teign (Lower) | ROOKERY BROOK |  |  | Commissioned in 2019 - full year data expected | 4.06 | 13 | 100
South West Water | BRIDGE HOUSE CSO | BRIDGE HOUSE_CSO_COLYFORD | 201881 | 201881/CS/01 | A1 | SO on sewer network | SY 2536 9266 | GB108045008880 | Umborne Brook | RIVER COLY (S) |  |  | EDM to be installed by December 2023
South West Water | BRIDGE HOUSE CSO | BRIDGE HSE_CSO_TIVERTON | 201823 | 201823 | A1 | SO on sewer network | SS 9532 1254 | GB108045015050 | Exe (Barle to Culm) | RIVER EXE |  |  | Commissioned in 2017 - full year data expected | 10.79 | 19 | 51 | Sensor failure / issue | Resolved - June
South West Water | BRIDGE PS / CSO / EO | BRIDGE SPST_PSCSOEO_PORTREATH | 300702 | 300702/PC/01 | A1 | Storm discharge at pumping station | SW 6610 4614 | 229 | #N/A | ATLANTIC OCEAN (C) |  | PORTREATH BEACH | Commissioned pre-2016 - full year data expected | 1783.51 | 94 | 100
South West Water | BRIDGE STREET QUAY CSO | BRIDGE STREET_CSO_KINGSBRIDGE | 203436 | 203436 | A1 | SO on sewer network | SX 7357 4402 | 69 | #N/A | KINGSBRIDGE ESTUARY(E) | Salcombe |  | Commissioned pre-2016 - full year data expected | 7.53 | 7 | 100
South West Water | BRIDGEND PUMPING STATION | BRIDGEND SPS_PSCSOEO_NEWTON FERRERS | 301628 | 301628 | A1 | Storm discharge at pumping station | SX 5547 4816 | 70 | #N/A | NEWTON CREEK (ESTUARINE) | Yealm |  | Commissioned in 2016 - full year data expected | 78.27 | 14 | 100
South West Water | STEAMER QUAY BRIDGETOWN CSO | BRIDGETOWN STEAMER QUAY_CSO_TOTNES | 201695 | 201695 | A1 | SO on sewer network | SX 8068 6020 | 23 | #N/A | RIVER DART ESTUARY | Dart |  | Commissioned in 2018 - full year data expected | 76.23 | 45 | 100
South West Water | BRIGHTLEY WOODS CSO | BRIGHTLEY WOODS_CSO_OKEHAMPTON | 201731 | 201731 | A1 | SO on sewer network | SX 5942 9687 | GB108050008110 | Middle River Okement | RIVER OKEMENT |  |  | Commissioned in 2018 - full year data expected | 45.43 | 34 | 100
South West Water | BRIXTON WASTEWATER TREATMENT WORKS | BRIXTON STW_SSO_BRIXTON | 302993 | 302993 | A2 | Storm tank at WwTW | SX 5544 5115 | GB108047004000 | Silverbridge Lake | BROAD OOZE, YEALM ESTUARY(E) | Yealm |  | Commissioned pre-2016 - full year data expected | 265.77 | 38 | 100
South West Water | BROADHEMBURY PUMPING STATION | BROADHEMBURY SPS_PSCSOEO_BROADHEMBURY | 201640 | 201640 | A1 | Storm discharge at pumping station | ST 0987 0467 | GB108045009200 | Tale | RIVER TALE |  |  | Commissioned in 2020 - full year data expected | 401 | 42 | 100
South West Water | BROADMEADOW PS | BROADMEADOW ESTATE SPS_PSCSOEO_TMOUTH | 203087 | 203087 | A1 | Storm discharge at pumping station | SX 9275 7291 | 22 | #N/A | TEIGN ESTUARY(E) | Teign |  | Commissioned pre-2016 - full year data expected | 3.12 | 1 | 100
South West Water | BROADWINDSOR WWTW | BROADWINDSOR STW_SO_BROADWINDSOR | NRA-SW-4946 | NRA-SW-4946 | A2 | Inlet SO at WwTW | ST 4328 0325 | GB108045014840 | Upper Axe | TRIBUTARY OF DRIMPTON STREAM |  |  | Commissioned in 2019 - full year data expected | 97.6 | 81 | 96
South West Water | BROADWINDSOR WWTW | BROADWINDSOR STW_SSO_BROADWINDSOR | NRA-SW-4946 | NRA-SW-4946 | A3 | Storm tank at WwTW | ST 4328 0325 | GB108045014840 | Upper Axe | TRIBUTARY OF DRIMPTON STREAM |  |  | Commissioned in 2019 - full year data expected | 673.96 | 41 | 100
South West Water | BROADWOODKELLY STW | BROADWOODKELLY STW_SSO_BROADWOODKELLY | 202216 | 202216/CS/01 | A2 | Storm tank at WwTW | SS 6121 0568 | GB108050014090 | Hole Brook | TRIBUTARY OF HOLE BROOK(S) |  |  | EDM to be installed by December 2023
South West Water | BROMPTON REGIS STW | BROMPTON REGIS STW_SO_BROMPTON REGIS | 202189/CS/01 | 202189/CS/01 | A2 | Inlet SO at WwTW | SS 9553 3119 | GB108045020910 | Pulham | PULHAM RIVER(S) |  |  | EDM to be installed by December 2023
South West Water | BROOK HOUSE SSO | BROOK HOUSE_CSO_DAWLISH | 200820 | 200820/CS/01 | A1 | SO on sewer network | SX 9544 7679 | GB108045008910 | Dawlish Water | DAWLISH WATER (S) |  | DAWLISH (TOWN) BEACH | Commissioned pre-2016 - full year data expected | 0.03 | 1 | 100
South West Water | DAWLISH SSO (BROOK STREET) | BROOK ST MANOR GARDENS_CSO_DAWLISH | 200821 | 200821/CS/01 | A1 | SO on sewer network | SX 9567 7674 | GB108045008910 | Dawlish Water | DAWLISH WATER(S) |  | DAWLISH (TOWN) BEACH | Commissioned pre-2016 - full year data expected | 16.17 | 26 | 100
South West Water | BRUNEL BRIDGE CSO | BRUNEL BRIDGE_CSO_SALTASH | 302583 | 302583 | A1 | SO on sewer network | SX 4338 5875 | 71 | #N/A | RIVER TAMAR (E) | Tamar |  | Commissioned pre-2016 - full year data expected | 7.52 | 29 | 100
South West Water | BRUSHFORD WWTW | BRUSHFORD STW_SO_BRUSHFORD | 203020 | 203020 | A2 | Inlet SO at WwTW | SS 9264 2589 | GB108045015100 | Lower Barle | RIVER BARLE |  |  | Commissioned in 2018 - full year data expected | 814.75 | 63 | 99
South West Water | BUCKERELL PUMPING STATION | BUCKERELL MANHOLE SPS_PSCSOEO_BUCKERELL | 201642 | 201642 | A1 | Storm discharge at pumping station | ST 1223 0085 | GB108045009170 | Lower River Otter | TRIBUTARY OF RIVER OTTER |  |  | Commissioned in 2020 - full year data expected | 2.84 | 2 | 100
South West Water | BUCKLAND MONACHORUM WWTW | BUCKLAND MONACHORUM STW_SSO_BUCKLAND MON | SWWA 877 | SWWA 877 | A2 | Storm tank at WwTW | SX 4868 6836 | GB108047007840 | Lower River Tavy | TRIBUTARY OF THE RIVER TAVY |  |  | Commissioned in 2018 - full year data expected | 1694.26 | 98 | 100 |  |  | Performance - Infiltration | Scheduled | Stage 1b: Confirmed "asset maintenance" issue
South West Water | BUCKLAND ST MARY STW | BUCKLAND ST MARY STW_SO_BUCKLAND ST MARY | NRA-SW-2517 | NRA-SW-2517 | A2 | Inlet SO at WwTW | ST 2669 1340 | GB108045015130 | Yarty | TRIBUTARY TO THE RIVER YARTY |  |  | EDM to be installed by December 2023
South West Water | BUCKLAND WASTEWATER TREATMENT WORKS | BUCKLAND STW_SSO_NEWTON ABBOT | 202009 | 202009 | A2 | Storm tank at WwTW | SX 9606 7143 | 22 | #N/A | ENGLISH CHANNEL (COASTAL) | Teign |  | Commissioned in 2018 - full year data expected | 802.97 | 70 | 100
South West Water | BUCKLEIGH PUMPING STATION | BUCKLEIGH SPS_PSCSOEO_NORTHAM | 200200 | 200200 | A1 | Storm discharge at pumping station | SS 4384 2823 | GB108050014500 | Kenwith Stream | SILFORD STREAM | Taw/Torridge |  | Commissioned in 2016 - full year data expected | 26.97 | 6 | 85 | Capital / maintenance works affect EDM operation | Resolved - February
South West Water | BUDDLE LANE CSO | BUDDLE LN_CSO_EXETER | 201931 | 201931 | A1 | SO on sewer network | SX 9300 9067 | 19 | #N/A | RIVER EXE VIA SWS | Exe |  | Commissioned in 2017 - full year data expected | 1.84 | 9 | 100
South West Water | BUDDLE LANE CSO | BUDDLE LN_CSO_HATHERLEIGH | 201774 | 201774 | A1 | SO on sewer network | SS 5405 0422 | GB108050008220 | Lower River Lew (Torridge) | RIVER LEW VIA SWS |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 100
South West Water | SUMMERLEAZE CAR PARK CSO | BUDE CAR PARK_CSO_BUDE | 301830 | 301830/CS/01 | A1 | SO on sewer network | SS 2074 0642 | GB108049007280 | Lower River Strat | BUDE BAY (C) |  | SUMMERLEAZE | Commissioned pre-2016 - full year data expected | 0 | 0 | 3 | Capital / maintenance works affect EDM operation | N/A - Ongoing investigation
South West Water | BULLEN STREET COMBINED SEWER OF | BULLEN ST_CSO_THORVERTON | 201825 | 201825 | A1 | SO on sewer network | SS 9259 0211 | GB108045015050 | Exe (Barle to Culm) | TRIB OF THE RIVER EXE VIA SWS |  |  | Commissioned in 2019 - full year data expected | 0.31 | 3 | 89 | Comms failure / issue | Resolved - August
South West Water | LOOE BULLER QUAY | BULLER QUAY_CSO_LOOE | 300973 | 300973/CS/01 | A1 | SO on sewer network | SX 2545 5338 | 74 | #N/A | LOOE RIVER (HARBOUR) (E) |  | EAST LOOE BEACH | Commissioned pre-2016 - full year data expected | 280.49 | 91 | 91 |  |  | Data collection - Tidal / river inundation | N/A - Ongoing investigation | N/A - Operational solution applied
South West Water | BULLER ROAD COMBINED SEWER OVERFLOW | BULLER ROAD_CSO_EXETER | EPRJB3294WU | EPR/JB3294WU | A1 | SO on sewer network | SX 9298 9063 | 19 | #N/A | RIVER EXE VIA SWS | Exe |  | Commissioned in 2017 - full year data expected | 465.6 | 26 | 95
South West Water | BUNKERS BRIDGE CSO | BUNKERS BRIDGE_CSO_CHUDLEIGH KNIGHTON | 201796 | 201796 | A1 | SO on sewer network | SX 8459 7722 | GB108046008540 | Teign (Lower) | TRIB OF THE RIVER TEIGN | Teign |  | Commissioned in 2018 - full year data expected | 33.3 | 23 | 77 | Comms failure / issue | Resolved - October
South West Water | BURLESCOMBE WWTW | BURLESCOMBE STW_SSO_BURLESCOMBE | NRA-SW-3474 | NRA-SW-3474 | A2 | Storm tank at WwTW | ST 0653 1698 | GB108045015020 | Spratford Stream | FENACRE WATER |  |  | Commissioned in 2019 - full year data expected | 130.08 | 17 | 100
South West Water | BURRINGTON STW | BURRINGTON STW_SSO_BURRINGTON | DRA 1437 | DRA 1437 | A2 | Storm tank at WwTW | SS 6357 1679 | GB108050014310 | Mully Brook | TRIB OF MULLY BROOK |  |  | EDM to be installed by December 2023
South West Water | BUTTS HILL PUMPING STATION | BUTTS HILL SPS_PSCSOEO_OTTERY ST MARY | 201378 | 201378 | A1 | Storm discharge at pumping station | SY 1005 9599 | GB108045009170 | Lower River Otter | GROUNDWATER VIA INFILT SYSTEM |  |  | Commissioned in 2020 - full year data expected | 23.91 | 16 | 100
South West Water | THE BUTTS PS | BUTTS SPST_PSCSOEO_KINGSTEIGNTON | 203343 | 203343 | A1 | Storm discharge at pumping station | SX 8714 7257 | 22 | #N/A | TRIB OF RIVER TEIGN(S) | Teign |  | Commissioned pre-2016 - full year data expected | 307.04 | 39 | 100
South West Water | BYES LANE COMBINED SEWER OVERFLOW | BYES LN_CSO_SIDFORD | 201837 | 201837 | A1 | SO on sewer network | SY 1372 8979 | GB108045009160 | Sid | RIVER SID VIA SWS |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 96
South West Water | CADELEIGH STW | CADELEIGH STW_SO_CADELEIGH | 202190/CS/01 | 202190/CS/01 | A2 | Inlet SO at WwTW | SS 9153 0812 | GB108045015010 | Dart (Exe) | UNNAMED WATERCOURSE(S) |  |  | EDM to be installed by December 2023
South West Water | CADGWITH NEW ROAD PSCSO/EO | CADGWITH SPS_PSCSOEO_CADGWITH | 301589 | 301589/PC/01 | A1 | Storm discharge at pumping station | SW 7215 1458 | 404 | #N/A | ENGLISH CHANNEL (C) |  |  | EDM to be installed by December 2023
South West Water | CAFFA MILL PUMPING STATION | CAFFA MILL SPS_PSCSOEO_FOWEY | 302774 | 302774 | A1 | Storm discharge at pumping station | SX 1276 5216 | 26 | #N/A | RIVER FOWEY ESTUARY(E) | Fowey | READYMONEY COVE | Commissioned pre-2016 - full year data expected | 461.2 | 138 | 100 |  |  | Data collection - Tidal / river inundation | N/A - Ongoing investigation | SOAF N/A - Proposed SFTP (overflow previously improved)
South West Water | CALENICK PUMPING STATION | CALENICK SPST_PSCSOEO_TRURO | 301590 | 301590 | A1 | Storm discharge at pumping station | SW 8219 4310 | GB108048001250 | Calenick Stream | RIVER TINNEY | Fal Estuary |  | Commissioned in 2016 - full year data expected | 5 | 2 | 100
South West Water | CALENICK STREET CSO | CALENICK ST REPEATER STATION_CSO_TRURO | 303088 | 303088 | A1 | SO on sewer network | SW 8251 4480 | GB108048002340 | Kenwyn | RIVER KENWYN VIA SWS | Fal Estuary |  | Commissioned in 2018 - full year data expected | 9.27 | 21 | 84 | Comms failure / issue | Resolved - April
South West Water | CALLINGTON WWTW | CALLINGTON STW_SSO_CALLINGTON | 303508 | 303508 | A3 | Storm tank at WwTW | SX 3405 6890 | GB108047007670 | Lower River Lynher | HAYE VALLEY STREAM |  |  | Commissioned in 2018 - full year data expected | 722.33 | 65 | 100
South West Water | CAMBRIDGE LANE COMBINED SEWER OF | CAMBRIDGE LANE_CSO_PLYMOUTH | 301740 | 301740 | A1 | SO on sewer network | SX 4697 5400 | 73 | #N/A | PLYMOUTH SOUND VIA SWS (ESTU.) |  | PLYMOUTH HOE (WEST) | Commissioned in 2016 - full year data expected | 57.04 | 57 | 100
South West Water | CAMELFORD WWTW | CAMELFORD STW_SO_CAMELFORD | 15/49/281/P/16 | 15/49/281/P/16 | A2 | Inlet SO at WwTW | SX 1058 8323 | GB108049007060 | Upper River Camel | RIVER CAMEL |  |  | Commissioned in 2017 - full year data expected | 358.5 | 34 | 100
South West Water | CAMELS HEAD WWTW | CAMELS HEAD STW_SO_PLYMOUTH | 303000 | 303000 | A2 | Inlet SO at WwTW | SX 4466 5714 | 73 | #N/A | WESTON MILL LAKE(E) | Tamar |  | Commissioned pre-2016 - full year data expected | 1106.38 | 71 | 100
South West Water | CAMELS HEAD WWTW | CAMELS HEAD STW_SSO_PLYMOUTH | 303000 | 303000 | A3 | Storm tank at WwTW | SX 4466 5714 | 73 | #N/A | WESTON MILL LAKE(E) | Tamar |  | Commissioned pre-2016 - full year data expected | 1007.1 | 67 | 100
South West Water | CAMPFIELD HILL CSO | CAMPFIELD HILL_CSO_TRURO | 302675 | 302675 | A1 | SO on sewer network | SW 8269 4496 | GB108048002330 | Lower River Allen (Fal) | RIVER ALLEN | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 1.5 | 4 | 94
South West Water | STOKENHAM CARAVAN PARK CSO | CARAVAN PARK_CSO_STOKENHAM | 201706 | 201706/CS/01 | A1 | SO on sewer network | SX 8126 4270 | GB108046004930 | The Gara | SLAPTON LEY (S) |  |  | EDM to be installed by December 2023
South West Water | CARNON DOWNS WWTW | CARNON DOWNS STW_SO_CARNON DOWNS | NRA-SW-7825 | NRA-SW-7825 | A2 | Inlet SO at WwTW | SW 7868 4000 | GB108048001231 | Lower River Carnon | CARNON RIVER | Fal Estuary |  | Commissioned in 2016 - full year data expected | 439.59 | 96 | 100
South West Water | CASTLE COPSE PUMPING STATION | CASTLE COPSE SPS_PSCSOEO_OTTERY ST MARY | 201379 | 201379 | A1 | Storm discharge at pumping station | SY 0748 9432 | GB108045009170 | Lower River Otter | TRIBUTARY OF RIVER OTTER |  |  | Commissioned in 2017 - full year data expected | 6.14 | 5 | 100
South West Water | WATERY LANE CSO | CASTLE HILL GARDENS_CSO_TORRINGTON | 200077/CS/01 | 200077 | A1 | SO on sewer network | SS 4992 1886 | GB108050014660 | Torridge (Lew to Estuary) | CASTLE HILL STREAM | Taw/Torridge |  | Commissioned in 2017 - full year data expected | 64.73 | 90 | 100
South West Water | 50 CASTLE PARK CSO | CASTLE PARK_CSO_HEMYOCK | 201851 | 201851/CS/01 | A1 | SO on sewer network | ST 1361 1358 | GB108045014980 | Middle Culm | STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | CASTLE PUMPING STATION | CASTLE SPST_PSCSOEO_BUDE | 301300 | 301300/PC/01 | A1 | Storm discharge at pumping station | SS 2064 0643 | 234 | #N/A | RIVER NEET (E) |  | SUMMERLEAZE | Commissioned pre-2016 - full year data expected | 2.33 | 1 | 95
South West Water | CASTLE STREET CSO | CASTLE ST_CSO_TRURO | 302671 | 302671 | A1 | SO on sewer network | SW 8233 4491 | GB108048002340 | Kenwyn | RIVER KENWYN(S) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | CATTEDOWN ROAD PUMPING STATION | CATTEDOWN ROAD SPS_PSCSOEO_PLYMOUTH | 300737 | 300737 | A1 | Storm discharge at pumping station | SX 4924 5343 | 73 | #N/A | PLYMOUTH SOUND (ESTUARINE) |  | PLYMOUTH HOE (EAST) | Commissioned pre-2016 - full year data expected | 89.04 | 32 | 100
South West Water | CATTLE MARKET CSO | CATTLE MARKET_CSO_SOUTH MOLTON | 201947 | 201947/CS/01 | A1 | SO on sewer network | SS 7175 2578 | GB108050014130 | Mole (Yeo to Burcombe Stream) | TRIB OF R. MOLE (S) |  |  | EDM to be installed by December 2023
South West Water | CAUSEWAY CLOSE CSO | CAUSEWAY CLOSE_CSO_NORTHAM | 302146 | 302146 | A1 | SO on sewer network | SS 4482 2980 | 199 | #N/A | TRIBUTARY OF THE PILL VIA SWS | Taw/Torridge |  | Commissioned in 2017 - full year data expected | 7.36 | 19 | 100
South West Water | CAVENDISH ROAD CSO | CAVENDISH RD_CSO_PLYMOUTH | 301764 | 301764 | A1 | SO on sewer network | SX 5003 5438 | 73 | #N/A | RIVER PLYM VIA SWS (ESTUARINE) |  |  | Commissioned in 2017 - full year data expected | 8.45 | 18 | 100
South West Water | CENTRAL PARK CSO | CENTRAL PARK_CSO_PLYMOUTH | 301744 | 301744 | A1 | SO on sewer network | SX 4622 5441 | 73 | #N/A | STONEHOUSE CREEK VIA SWS (EST) |  |  | Commissioned pre-2016 - full year data expected | 11.17 | 22 | 100
South West Water | WOLSELEY ROAD TANK CSO | CENTRAL RESERVATION_CSO_PLYMOUTH | 302609 | 302609 | A1 | SO on sewer network | SX 4486 5787 | 73 | #N/A | WESTON MILL CREEK VIA WTR CRSE | Tamar |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | CENTRAL STATION YARD CSO | CENTRAL STATION YARD_CSO_EXETER | 201370 | 201370 | A1 | SO on sewer network | SX 9147 9250 | GB108045009040 | Exe (Creedy to Estuary) | HIGHER LEAT VIA SWS | Exe |  | Commissioned in 2018 - full year data expected | 0 | 1 | 99
South West Water | PLYMOUTH CENTRAL STW | CENTRAL STW SHAFT 16 SPST_PSCSOEO_PLYMOU | 303347 | 303347 | A1 | Storm discharge at pumping station | SX 4991 5394 | 73 | #N/A | PLYMOUTH SOUND/PLYM ESTUARY(E) |  | PLYMOUTH HOE (EAST) | Commissioned pre-2016 - full year data expected | 927.53 | 120 | 100
South West Water | CHACEWATER STW | CHACEWATER STW_SO_CHACEWATER | NRA-SW-6619 | NRA-SW-6619 | A2 | Inlet SO at WwTW | SW 7527 4409 | GB108048001160 | Upper Carnon River | (S) RIVER CARNON | Fal Estuary |  | Commissioned in 2020 - full year data expected | 272.21 | 30 | 100
South West Water | CHACEWATER STW | CHACEWATER STW_SSO_CHACEWATER | NRA-SW-6619 | NRA-SW-6619 | A3 | Storm tank at WwTW | SW 7527 4409 | GB108048001160 | Upper Carnon River | (S) RIVER CARNON | Fal Estuary |  | Commissioned in 2020 - full year data expected | 2366.32 | 120 | 100
South West Water | CHAGFORD FIRE 1 CSO | CHAGFORD FIRE 1_CSO_CHAGFORD | 201798 | 201798 | A1 | SO on sewer network | SX 7047 8785 | GB108046008550 | Teign (Upper) | TRIB OF RIVER TEIGN |  |  | Commissioned in 2018 - full year data expected | 9.7 | 22 | 71 | Comms failure / issue | Resolved - October
South West Water | CHAGFORD FIRE 2 CSO | CHAGFORD FIRE 2_CSO_CHAGFORD | 201789 | 201789 | A1 | SO on sewer network | SX 7051 8790 | GB108046008550 | Teign (Upper) | TRIB OF THE RIVER TEIGN |  |  | Commissioned in 2018 - full year data expected | 141.4 | 91 | 100
South West Water | CHAGFORD WASTEWATER TREATMENT WORKS | CHAGFORD MAIN STW_SO_CHAGFORD | SWWA 1137 | SWWA 1137 | A2 | Inlet SO at WwTW | SX 7007 8817 | GB108046008550 | Teign (Upper) | RIVER TEIGN |  |  | Commissioned in 2017 - full year data expected | 461.98 | 75 | 98
South West Water | CHALLABOROUGH PSCSO/EO | CHALLABOROUGH SPST_PSCSOEO_CHALLABOROUGH | 202602 | 202602 | A1 | Storm discharge at pumping station | SX 6488 4494 | 266 | #N/A | CHALLABOROUGH STREAM(S) |  | CHALLABOROUGH BEACH | Commissioned in 2020 - full year data expected | 0.62 | 9 | 100
South West Water | CHAPEL AMBLE WWTW | CHAPEL AMBLE S T SEPTNK_SO_CHAPEL AMBLE | EPRCP3528XH | EPR/CP3528XH | A2 | Inlet SO at WwTW | SW 9979 7526 | GB108049006910 | Amble | RIVER AMBLE |  |  | Commissioned in 2017 - full year data expected | 341.37 | 28 | 100
South West Water | CHAPEL LANE COMBINED SEWER OVERFLOW | CHAPEL LANE OTTERY ST MARY CSO | 201382 | 201382 | A1 | SO on sewer network | SY 1014 9551 | GB108045009170 | Lower River Otter | TRIBUTARY OF THE RIVER OTTER |  |  | Commissioned in 2019 - full year data expected | 3.16 | 16 | 72 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | CHAPEL LANE CSO | CHAPEL LN_CSO_HORRABRIDGE | 301847 | 301847/CS/01 | A1 | SO on sewer network | SX 5131 6992 | GB108047007870 | Walkham | RIVER WALKHAM (S) |  |  | EDM to be installed by December 2023
South West Water | CHAPEL STREET CSO | CHAPEL STREET_CSO_AXMOUTH | 201885 | 201885 | A1 | SO on sewer network | SY 2581 9109 | 17 | #N/A | TRIB OF RIVER AXE |  |  | Commissioned in 2019 - full year data expected | 6.97 | 7 | 100
South West Water | CHAPELDOWN PUMPING STATION | CHAPELDOWN SPST_PSCSOEO_TORPOINT | 15/48/16/P/13 | 15-48-16-P-13 | A1 | Storm discharge at pumping station | SX 4372 5458 | 72 | #N/A | PLYMOUTH SOUND (ESTUARINE) |  |  | Commissioned in 2016 - full year data expected | 52.65 | 47 | 100
South West Water | CHARD ROAD COMBINED SEWER OVERFLOW | CHARD ROAD_CSO_AXMINSTER | DRA 1560 | DRA 1560 | A1 | SO on sewer network | SY 2989 9949 | GB108045008870 | Lower Axe | RIVER AXE |  |  | Commissioned in 2020 - full year data expected | 351 | 44 | 86 | Comms failure / issue | Resolved - May
South West Water | CHARLESTOWN HARBOUR PSCSO/EO | CHARLESTN REMOTE SPS_PSCSOEO_ST AUSTELL | 301635 | 301635/PC/01 | A1 | Storm discharge at pumping station | SX 0392 5424 | GB108048001330 | Crinnis River | ST AUSTELL BAY (C) |  | CHARLESTOWN BEACH | Commissioned pre-2016 - full year data expected | 20.55 | 23 | 100
South West Water | CHARLESTOWN PUMPING STATION | CHARLESTOWN SPS_PSCSOEO_CHARLESTOWN | 032051/PC/01 | 32051 | A1 | Storm discharge at pumping station | SX 0387 5120 | 256 | #N/A | ST AUSTELL BAY, ENGLISH CHANEL |  | CHARLESTOWN BEACH | Commissioned in 2017 - full year data expected | 37.02 | 21 | 100
South West Water | ILFRACOMBE RESEWERAGE | CHEYNE BEACH SPST_PSCSOEO_ILFRACOMBE | 004369/PC/01 | 004369/PC/01 | A1 | Storm discharge at pumping station | SS 5226 4798 | 237 | #N/A | BRISTOL CHANNEL |  | ILFRACOMBE WILDERSMOUTH BEACH | Commissioned pre-2016 - full year data expected | 8.79 | 10 | 100
South West Water | #TBC | CHICHESTER SCREENS_CSO_NEWTON ABBOT | #TBC | #TBC | A1 | SO on sewer network | SX 87375 71545 | GB510804605800 | TEIGN | #TBC |  |  | EDM to be installed by December 2023
South West Water | HOME CLOSE PUMPING STATION | CHILLINGTON SPS_PSCSOEO_CHILLINGTON | 202168 | 202168 | A1 | Storm discharge at pumping station | SX 7949 4265 | GB108046004760 | Avon (DevonTidal) and Sth Hams - Frogmore | FROGMORE STREAM (VIA SWS) | Salcombe |  | Commissioned in 2016 - full year data expected | 0 | 0 | 97
South West Water | CHILLINGTON & FROGMORE STW | CHILLINGTON STW_SSO_CHILLINGTON | 203442 | 203442 | A2 | Storm tank at WwTW | SX 7836 4263 | GB108046004760 | Avon (DevonTidal) and Sth Hams - Frogmore | CHILLINGTON STREAM(S) | Salcombe |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | CHILSWORTHY WWTW | CHILSWORTHY STW_SO_GUNNISLAKE | SWWA 569 | SWWA 569 | A2 | Inlet SO at WwTW | SX 4175 7260 | GB108047007860 | Lower River Tamar | RIVER TAMAR |  |  | Commissioned in 2019 - full year data expected | 4139.97 | 316 | 100
South West Water | CHITTLEHAMHOLT STW | CHITTLEHAMHOLT STW_SO_CHITTLEHAMHOLT | NRA-SW-6748 | NRA-SW-6748/SO/01 | A2 | Inlet SO at WwTW | SS 6474 2110 | GB108050014530 | Taw (River Mole to Estuary) | (S) TRIB OF CLAYTON STREAM |  |  | EDM to be installed by December 2023
South West Water | CHITTLEHAMPTON WWTW | CHITTLEHAMPTON STW_SSO_CHITTLEHAMPTON | NRA-SW-7809 | NRA-SW-7809 | A2 | Storm tank at WwTW | SS 6350 2521 | GB108050014520 | Hawkridge Brook | TRIB OF HAWKBRIDGE BROOK |  |  | Commissioned in 2017 - full year data expected | 1803.42 | 116 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP7 or Green Recovery
South West Water | CHRISTOW WASTEWATER TREATMENT WORKS | CHRISTOW STW_SSO_TEIGN VALLEY | NRA-SW-6620 | NRA-SW-6620 | A2 | Storm tank at WwTW | SX 8405 8538 | GB108046008540 | Teign (Lower) | RIVER TEIGN |  |  | Commissioned in 2016 - full year data expected | 1914.53 | 97 | 96
South West Water | CHUDLEIGH KNIGHTON WWTW | CHUDLEIGH KNIGHTON STW_SO_CHUDLEIGH K | 203388 | 203388 | A2 | Inlet SO at WwTW | SX 8465 7716 | GB108046008540 | Teign (Lower) | RIVER TEIGN | Teign |  | Commissioned in 2017 - full year data expected | 152.06 | 50 | 100
South West Water | CHUDLEIGH KNIGHTON WWTW | CHUDLEIGH KNIGHTON STW_SSO_CHUDLEIGH K | 203388 | 203388 | A3 | Storm tank at WwTW | SX 8465 7716 | GB108046008540 | Teign (Lower) | RIVER TEIGN | Teign |  | Commissioned in 2017 - full year data expected | 455.86 | 41 | 100
South West Water | CHUDLEIGH WWTW | CHUDLEIGH STW_SO_NEWTON ABBOT | NRA-SW-6984 | NRA-SW-6984 | A2 | Inlet SO at WwTW | SX 8614 7937 | GB108046008540 | Teign (Lower) | RIVER TEIGN | Teign |  | Commissioned in 2016 - full year data expected | 478.84 | 161 | 100
South West Water | CHUDLEIGH WWTW | CHUDLEIGH STW_SSO_NEWTON ABBOT | NRA-SW-6984 | NRA-SW-6984 | A3 | Storm tank at WwTW | SX 8604 7934 | GB108046008540 | Teign (Lower) | RIVER TEIGN | Teign |  | Commissioned in 2016 - full year data expected | 1247.72 | 87 | 93 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
South West Water | CHURCH COVE ROAD PS | CHURCH COVE RD SPS_PSCSOEO_CHURCH COVE | 302945 | 302945 | A1 | Storm discharge at pumping station | SW 7146 1275 | GB650806330000 | Fal / Helford | CHURCH COVE (C) |  |  | EDM to be installed by December 2023
South West Water | CHURCH LANE CSO | CHURCH LANE_CSO_TAVISTOCK | 301887 | 301887 | A1 | SO on sewer network | SX 4783 7397 | GB108047007840 | Lower River Tavy | RIVER TAVY VIA SWS |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 100
South West Water | CHURCH LANE COMBINED SEWER OVERFLOW | CHURCH LN_CSO_CREDITON | 201870 | 201870 | A1 | SO on sewer network | SS 8448 0041 | GB108045009090 | Middle Creedy | TRIB OF RIVER CREEDY VIA SWS |  |  | Commissioned in 2018 - full year data expected | 0.5 | 5 | 94
South West Water | CHURCH ROAD JCT OF CECIL ROAD CSO | CHURCH RD/CECIL RD_CSO_EXETER | 201915 | 201915 | A1 | SO on sewer network | SX 9299 9067 | 19 | #N/A | RIVER EXE VIA SWS | Exe |  | Commissioned in 2018 - full year data expected | 12.77 | 14 | 100
South West Water | CHURCH ROAD CSO | CHURCH ROAD SSO_CSO_WHIMPLE | 203623 | 203623 | A1 | SO on sewer network | SY 0416 9713 | GB108045008810 | Upper Cranny Brook | CRANNY BROOK | Exe |  | Commissioned in 2018 - full year data expected | 47.57 | 8 | 100
South West Water | CHURCH ROAD CSO | CHURCH ROAD_CSO_ALPHINGTON | 201933 | 201933 | A1 | SO on sewer network | SX 9176 9027 | GB108045009020 | Alphin Brook | ALPHIN BROOK | Exe |  | Commissioned in 2018 - full year data expected | 14.8 | 34 | 100
South West Water | STOCKMEADOW HOUSE CSO | CHURCH ROAD_CSO_BISHOPSTEIGNTON | 203350 | 203350 | A1 | SO on sewer network | SX 9107 7348 | 22 | #N/A | TRIBUTARY O TEIGN ESTUARY(S) | Teign |  | Commissioned pre-2016 - full year data expected | 51.65 | 44 | 100
South West Water | CHURCH SQUARE CSO | CHURCH SQUARE_CSO_MENHENIOT | 301858 | 301858 | A1 | SO on sewer network | SX 2845 6235 | GB108048002320 | Seaton | TRIBUTARY OF THE RIVER SEATON |  | SEATON BEACH (CORNWALL) | Commissioned pre-2016 - full year data expected | 3.7 | 9 | 98
South West Water | CHURCH STREET COMBINED SEWER OVERFL | CHURCH ST_CSO_CREDITON | 201864 | 201864 | A1 | SO on sewer network | SS 8448 0041 | GB108045009090 | Middle Creedy | TRIB OF RIVER CREEDY (SWS) |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 100
South West Water | CHURCH WAY CSO | CHURCH WAY_CSO_YEALMPTON | 301894 | 301894 | A1 | SO on sewer network | SX 5775 5158 | GB108047004010 | Lower River Yealm | RIVER YEALM | Yealm |  | Commissioned in 2018 - full year data expected | 0 | 0 | 60 | Sensor failure / issue | Resolved - October
South West Water | MARLDON (CHURSCOMBE CROSS) PS | CHURSCOMBE CROSS SPS_PSCSOEO_MARLDON | 201586 | 201586 | A1 | Storm discharge at pumping station | SX 8712 6258 | 429 | #N/A | KIRKHAM STREAM |  | PAIGNTON (PRESTON SANDS) | Commissioned pre-2016 - full year data expected | 49.63 | 23 | 100
South West Water | ALBERT PIER PUMPING STATION | CHYANDOUR SPST_PSCSOEO_PENZANCE | NRA-SW-5354 | NRA-SW-5354 | A1 | Storm discharge at pumping station | SW 4773 3038 | 405 | #N/A | MOUNTS BAY |  | LONG ROCK | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | CLAPTON PUMPING STATION | CLAPTON SPS_PSCSOEO_CREWKERNE | 203475 | 203475 | A1 | Storm discharge at pumping station | ST 4131 0639 | GB108045014840 | Upper Axe | CLAPTON STREAM |  |  | Commissioned in 2017 - full year data expected | 15.53 | 5 | 100
South West Water | CLAWTON STW | CLAWTON STW_SO_CLAWTON | 303598 | 303598 | A2 | Inlet SO at WwTW | SX 3534 9910 | GB108047008060 | Claw | TRIB OF RIVER CLAW(S) |  |  | EDM to be installed by December 2023
South West Water | CLEARBROOK STW | CLEARBROOK STW_SSO_CLEARBROOK | NRA-SW-3027 | NRA-SW-3027 | A2 | Storm tank at WwTW | SX 5255 6547 | GB108047003660 | Meavy | (S) TRIB OF RIVER MEAVY |  |  | EDM to be installed by December 2023
South West Water | LOWER CLEAVE PSCSO/EO | CLEAVE SPS_PSCSOEO_NORTHAM | 201621 | 201621/PC/01 | A1 | Storm discharge at pumping station | SS 4558 2815 | 199 | #N/A | RIVER TORRIDGE (E) | Taw/Torridge |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | CLEMENTS FARM PUMPING STATION | CLEMENTS FARM SPS_PSCSOEO_TORQUAY | 201622 | 201622 | A1 | Storm discharge at pumping station | SX 9005 6620 | GB108046005330 | Aller Brook (Teign) - Upper | TRIB OF ALLER BROOK |  |  | Commissioned in 2016 - full year data expected | 961.49 | 49 | 82 | Comms failure / issue | Resolved - November
South West Water | CLENNON VALLEY PUMPING STATION | CLENNON VALLEY SPS_PSCSO_PAIGNTON | 201396 | 201396 | A1 | SO on sewer network | SX 8984 6036 | 429 | #N/A | ENGLISH CHANNEL |  | PAIGNTON (PAIGNTON SANDS) | Commissioned pre-2016 - full year data expected | 94.78 | 16 | 100
South West Water | CLENNON VALLEY PUMPING STATION | CLENNON VALLEY SPS_PSCSO_PAIGNTON | 201396 | 201396 | A1 | SO on sewer network | SX 8939 6040 | 429 | #N/A | ENGLISH CHANNEL |  | PAIGNTON (PAIGNTON SANDS) | Commissioned pre-2016 - full year data expected | 41.2 | 11 | 100
South West Water | CLENNON VALLEY PUMPING STATION | CLENNON VALLEY SPS_PSCSO_PAIGNTON | 201396 | 201396 | A1 | SO on sewer network | SX 8951 5955 | 429 | #N/A | ENGLISH CHANNEL |  | GOODRINGTON BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 44 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | CLIFTON ROAD/JCT ALBERT ROAD CSO | CLIFTON RD/ALBERT RD_CSO_EXETER | 201918 | 201918 | A1 | SO on sewer network | SX 9223 9188 | GB108045009040 | Exe (Creedy to Estuary) | RIVER EXE VIA SWS | Exe |  | Commissioned in 2017 - full year data expected | 0.14 | 1 | 100
South West Water | CHUTE STREET CSO | CLIFTON RD/CHUTE ST_CSO_EXETER | 201919 | 201919 | A1 | SO on sewer network | SX 9223 9189 | GB108045009040 | Exe (Creedy to Estuary) | RIVER EXE VIA SWS | Exe |  | Commissioned in 2017 - full year data expected | 28.25 | 5 | 100
South West Water | WEST BRIDGE CSO | CLINIC_CSO_TAVISTOCK | 300078/CS/01 | 300078 | A1 | SO on sewer network | SX 4765 7373 | GB108047007840 | Lower River Tavy | RIVER TAVY |  |  | Commissioned in 2017 - full year data expected | 101.7 | 42 | 73 | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
South West Water | CLOCKTOWER CSO | CLOCK TOWER_CSO_NEWTON ABBOT | 203335 | 203335 | A1 | SO on sewer network | SX 8578 7130 | GB108046008450 | Lemon | RIVER LEMON(S) | Teign |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | CLYST HONITON PUMPING STATION | CLYST HONITON SPS_PSCSO_EXETER | 201611 | 201611 | A1 | SO on sewer network | SX 9865 9369 | GB108045008860 | Upper Clyst | RIVER CLYST | Exe |  | Commissioned in 2016 - full year data expected | 104.93 | 12 | 100
South West Water | COACH ROAD CSO | COACH RD_CSO_NEWTON ABBOT | 203095 | 203095 | A1 | SO on sewer network | SX 8596 7024 | GB108046005350 | Aller Brook (Teign) - Lower | THE WOLBOROUGH STREAM (S) | Teign |  | Commissioned pre-2016 - full year data expected | 2.38 | 6 | 100
South West Water | ILSHAM ROAD CSO | COCKINGTON LANE SPS_PSCSOEO_TORQUAY | 200223 | 200223 | A1 | Storm discharge at pumping station | SX 9039 6304 | 429 | #N/A | ILSHAM VALLEY STREAM |  | TORRE ABBEY BEACH | Commissioned pre-2016 - full year data expected | 10.62 | 5 | 100
South West Water | ILSHAM ROAD CSO | COCKINGTON LANE SPS_PSCSOEO_TORQUAY | 200223 | 200223 | A1 | Storm discharge at pumping station | SX 9039 6304 | 429 | #N/A | ILSHAM VALLEY STREAM |  | TORRE ABBEY BEACH | Commissioned pre-2016 - full year data expected | 10.62 | 5 | 100
South West Water | COCKWOOD PSEO | COCKWOOD SPS_PSCSOEO_DAWLISH | 202629 | 202629 | A1 | Storm discharge at pumping station | SX 9756 8073 | 20 | #N/A | COFTON STREAM(S) | Exe |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | COFTON PSCSO/EO | COFTON SPS_PSCSOEO_DAWLISH | 202627 | 202627 | A1 | Storm discharge at pumping station | SX 9712 8061 | 20 | #N/A | COFTON STREAM(S) | Exe |  | Commissioned in 2016 - full year data expected | 58.88 | 11 | 51 | Sensor failure / issue | Resolved - December
South West Water | COINAGEHALL STREET CSO | COINAGEHALL ST_CSO_HELSTON | 034260/CS/01 | 34260 | A1 | SO on sewer network | SW 6553 2731 | GB108048001172 | Lower River Cober | RIVER COBER VIA SWS |  |  | Commissioned in 2020 - full year data expected | 87.11 | 77 | 100
South West Water | COLATON RALEIGH COMBINED SEWER OF | COLATON RALEIGH SSO_CSO_COLATON RALEIGH | 201882 | 201882 | A1 | SO on sewer network | SY 0844 8704 | 18 | #N/A | TRIB OF THE RIVER OTTER |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 100
South West Water | COLLETON GROVE CSO | COLLETON GROVE_CSO_EXETER | 201927 | 201927 | A1 | SO on sewer network | SX 9223 9189 | GB108045009040 | Exe (Creedy to Estuary) | RIVER EXE VIA SWS | Exe |  | Commissioned in 2018 - full year data expected | 28.33 | 18 | 100
South West Water | COLYFORD PSCSO/EO | COLYFORD SPST_PSCSOEO_COLYFORD | 201643 | 201643/PC/01 | A1 | Storm discharge at pumping station | SY 2535 9266 | GB108045008880 | Umborne Brook | RIVER COLY(S) |  |  | EDM to be installed by December 2023
South West Water | FIRE STATION CSO | COLYTON FIRE STATION_CSO_COLYTON | 201879 | 201879/CS/01 | A1 | SO on sewer network | SY 2478 9378 | GB108045008880 | Umborne Brook | RIVER COLY (S) |  |  | EDM to be installed by December 2023
South West Water | COLYTON & COLYFORD WWTW | COLYTON STW_SSO_COLYTON | DRA 441 | DRA 441 | A2 | Storm tank at WwTW | SY 2592 9270 | GB108045008870 | Lower Axe | RIVER AXE |  |  | Commissioned in 2019 - full year data expected | 858.63 | 74 | 100
South West Water | COLYTON CHANTRY CSO | COLYTON_CSO_COLYTON | NRA-SW-1138 | NRA-SW-1138 | A1 | SO on sewer network | SY 2458 9423 | GB108045008790 | Lower Coly | RIVER COLY |  |  | EDM to be installed by December 2023
South West Water | COMBREW LANE CSO | COMBREW LANE_CSO_BARNSTAPLE | 203290 | 203290 | A1 | SO on sewer network | SS 5266 3238 | 198 | #N/A | BRYN BROOK(S) | Taw/Torridge |  | Commissioned pre-2016 - full year data expected | 42.54 | 20 | 100
South West Water | 20 COMMERCIAL ROAD | COMMERCIAL RD/PLACE_CSO_PLYMOUTH | 301718 | 301718/CS/01 | A1 | SO on sewer network | SX 4923 5343 | 73 | #N/A | CATTEWATER (C) |  | PLYMOUTH HOE (EAST) | Commissioned pre-2016 - full year data expected | 0 | 0 | 97
South West Water | 20 COMMERCIAL ROAD | COMMERCIAL RD_CSO_PLYMOUTH | 302147 | 302147/CS/01 | A1 | SO on sewer network | SX 4883 5381 | 73 | #N/A | PLYMOUTH SOUND (C) |  | PLYMOUTH HOE (EAST) | Commissioned pre-2016 - full year data expected | 0 | 0 | 40 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | COMMERCIAL ROAD PUMPING STATION | COMMERCIAL ROAD SPS_PSCSOEO_PENRYN | 303007 | 303007 | A1 | Storm discharge at pumping station | SW 7879 3443 | 402 | #N/A | THE PENRYN RIVER (E) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 450.63 | 100 | 89 | Comms failure / issue | Resolved - June
South West Water | COMMINUTOR HOUSE CSO | COMMINUTOR HOUSE GOULD RD_CSO_SALCOMBE | 003218/CS/01 | 003218/CS/01 | A1 | SO on sewer network | SX 7389 3928 | 69 | #N/A | SHADYCOMBE CREEK |  | MILL BAY BEACH | Commissioned pre-2016 - full year data expected | 234.07 | 103 | 100
South West Water | COMPTON AND MARLDON WWTW | COMPTON & MARLDON STW_SO_COMPTON | DRA 1130 | DRA 1130 | A2 | Inlet SO at WwTW | SX 8634 6582 | GB108046005340 | Aller Brook | TRIB OF THE ALLER BROOK | Teign |  | Commissioned in 2017 - full year data expected | 287.62 | 29 | 100
South West Water | COMPTON CASTLE CSO | COMPTON CASTLE_CSO_COMPTON | 201791 | 201791 | A1 | SO on sewer network | SX 8649 6533 | GB108046005340 | Aller Brook | TRIB OF ALLER BROOK | Teign |  | Commissioned in 2017 - full year data expected | 1033.55 | 112 | 98
South West Water | CONSTANTINE BRIDGE PUMPING STATION | CONSTANTINE BRIDGE SPS_PSCSOEO_FALMOUTH | 302096 | 302096 | A1 | Storm discharge at pumping station | SW 7292 2902 | 75 | #N/A | NANCEROY STREAM (S) | Helford |  | Commissioned pre-2016 - full year data expected | 55.88 | 22 | 83 | Comms failure / issue | Resolved - June
South West Water | CONSTANTINE STW | CONSTANTINE STW_SO_CONSTANTINE | 302487 | 302487 | A2 | Inlet SO at WwTW | SW 7368 2886 | GB108048001870 | Lestraines River | LESTRAINES RIVER(S) | Helford |  | Commissioned pre-2016 - full year data expected | 89.14 | 51 | 100
South West Water | COOKS CROSS COMBINED SEWER OVERFLOW | COOKS CROSS_CSO_SOUTH MOLTON | 201946 | 201946 | A1 | SO on sewer network | SS 7083 2569 | GB108050013950 | Nadrid Water | TRIB OF NARDRIDWATER VIA SWS |  |  | Commissioned in 2018 - full year data expected | 3.06 | 15 | 100
South West Water | COOMBE ROAD CSO | COOMBE ROAD_CSO_SALTASH | 302584 | 302584 | A1 | SO on sewer network | SX 4288 5845 | 71 | #N/A | RIVER TAMAR ESTUARY(E) | Tamar |  | Commissioned pre-2016 - full year data expected | 18.82 | 15 | 95
South West Water | COMBEINTEIGNHEAD PUMPING STATION | COOMBETEIGNHEAD SPS_PSCSOEO_COOMBETEIGN | 002659/PC/01 | 2659 | A1 | Storm discharge at pumping station | SX 9013 7176 | 22 | #N/A | COMBE STREAM |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 100
South West Water | CORNER LANE PUMPING STATION | CORNER LANE SPS_PSCSOEO_HALBERTON | 201648 | 201648 | A1 | Storm discharge at pumping station | ST 0074 1282 | GB108045014960 | Halberton Stream | TRIBUTARY OF SPRATFORD STREAM |  |  | Commissioned in 2018 - full year data expected | 301.55 | 65 | 100
South West Water | CORNWALL BEACH (PS3) | CORNWALL BEACH SPS_PSCSO_PLYMOUTH | 301987 | 301987 | A1 | SO on sewer network | SX 4475 5469 | 73 | #N/A | RIVER TAMAR (ESTUARINE) |  |  | Commissioned in 2017 - full year data expected | 10.48 | 5 | 100
South West Water | CORNWOOD PUMPING STATION | CORNWOOD SPST_PSCSOEO_LUTTON | 300617 | 300617/PC/01 | A1 | Storm discharge at pumping station | SX 6080 5940 | GB108047004050 | Upper River Yealm | RIVER YEALM (S) |  |  | EDM to be installed by December 2023
South West Water | CORNWORTHY STW | CORNWORTHY STW_SSO_DARTMOUTH | 200926 | 200926 | A2 | Storm tank at WwTW | SX 8260 5569 | 23 | #N/A | TRIB OF THE DART ESTUARY | Dart |  | Commissioned in 2016 - full year data expected | 1212.24 | 119 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP7 or Green Recovery
South West Water | COT VALLEY PUMPING STATION | COT VALLEY_PSCSOEO_ST JUST | 303092 | 303092 | A1 | Storm discharge at pumping station | SW 3550 3100 | 230 | #N/A | ATLANTIC / PORTH NANVEN STREAM |  |  | Commissioned in 2019 - full year data expected | 746.84 | 42 | 59 | Comms failure / issue | Resolved - November
South West Water | COULSON PARK PUMPING STATION | COULSONS PARK SPST_PSCSOEO_LOSTWITHIEL | NRA-SW-5460 | NRA-SW-5460 | A1 | Storm discharge at pumping station | SX 1049 5942 | 26 | #N/A | RIVER FOWEY (ESTUARINE) | Fowey |  | Commissioned pre-2016 - full year data expected | 1733.23 | 115 | 100
South West Water | EXETER (COUNTESS WEAR) STW | COUNTESS WEAR STW_SO_EXETER | 202475 | 202475 | A2 | Inlet SO at WwTW | SX 9479 8924 | 20 | #N/A | RIVER EXE ESTUARY(E) | Exe |  | Commissioned pre-2016 - full year data expected | 110.59 | 25 | 100
South West Water | EXETER (COUNTESS WEAR) STW | COUNTESS WEAR STW_SSO_EXETER | 202475 | 202475 | A3 | Storm tank at WwTW | SX 9497 8905 | 20 | #N/A | RIVER EXE ESTUARY(E) | Exe |  | Commissioned pre-2016 - full year data expected | 123.04 | 47 | 100
South West Water | COURT BARTON FARM CSO | COURT BARTON FARM_CSO_LAPFORD | 201846 | 201846/CS/01 | A1 | SO on sewer network | SS 7361 0762 | GB108050014650 | Dalch | RIVER DALCH (S) |  |  | EDM to be installed by December 2023
South West Water | COURTWOOD ROAD PSCSO/EO | COURTWOOD SPS_PSCSOEO_NEWTON FERRERS | 302462 | 302462 | A1 | Storm discharge at pumping station | SX 5393 4831 | 70 | #N/A | RIVER YEALM ESTUARY (E) | Yealm |  | Commissioned pre-2016 - full year data expected | 1.33 | 7 | 100
South West Water | COVE PUMPING STATION | COVE BOAT POUND SPS_PSCSOEO_ST AGNES | 303457 | 303457 | A1 | Storm discharge at pumping station | SW 7217 5154 | 229 | #N/A | TREVAUNANCE STREAM(S) |  | TREVAUNANCE COVE BEACH | Commissioned pre-2016 - full year data expected | 15.81 | 16 | 82 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | COVERACK HARBOUR PSEO/CSO | COVERACK HARBOUR SPS_PSCSOEO_THE LIZARD | 301387 | 301387 | A1 | Storm discharge at pumping station | SW 7853 1823 | 404 | #N/A | COVERACK COVE (C) |  | COVERACK BEACH | Commissioned pre-2016 - full year data expected | 20.27 | 22 | 98
South West Water | COVERACK MILL PS | COVERACK MILL SPST_PSCSOEO_THE LIZARD | 301388 | 301388 | A1 | Storm discharge at pumping station | SW 7823 1839 | 404 | #N/A | COVERACK COVE(C) |  | COVERACK BEACH | Commissioned pre-2016 - full year data expected | 38.07 | 19 | 100
South West Water | COWDRY CLOSE CSO | COWDRAY CLOSE_CSO_SALTASH | 302590 | 302590 | A1 | SO on sewer network | SX 4232 5866 | 71 | #N/A | RIVER TAMAR ESTUARY (E) | Tamar |  | Commissioned pre-2016 - full year data expected | 13.4 | 8 | 100
South West Water | CRANTOCK (BEACH ROAD) SPS | CRANTOCK BEACH SPS_PSCSOEO_CRANTOCK | 301324 | 301324/PC/01 | A1 | Storm discharge at pumping station | SW 7890 6079 | 197 | #N/A | CRANTOCK BEACH (C) |  | CRANTOCK BEACH | Commissioned pre-2016 - full year data expected | 25.44 | 4 | 100
South West Water | CREAKAVOSE PARK PSCSO/EO | CREAKAVOSE SPS_PSCSOEO_ST STEPHEN | 302097 | 302097/PC/01 | A1 | Storm discharge at pumping station | SW 9387 5345 | GB108048001390 | Upper River Fal | UN-NAMED WATERCOURSE (S) |  |  | EDM to be installed by December 2023
South West Water | CROCKERNWELL SEWAGE TREATMENT WORKS | CROCKERNWELL STW_SO_TEDBURN | 203889 | 203889 | A2 | Inlet SO at WwTW | SX 7557 9242 | GB108046008600 | Scotley Brook | SCOTLEY BROOK(S) |  |  | EDM to be installed by December 2023
South West Water | FULFORD COTTAGES CSO | CROCKERNWELL_CSO_CROCKERNWELL | 201790 | 201790/CS/01 | A1 | SO on sewer network | SX 7566 9242 | GB108046008600 | Scotley Brook | STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | CROOKLETS CAR PARK CSO | CROOKLETS_CSO_BUDE | 301831 | 301831/CS/01 | A1 | SO on sewer network | SS 2041 0714 | 234 | #N/A | RIVER NEET (S) |  | CROOKLETS | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | COMBE MARTIN BEACH PUMPING STATION | CROSS STREET SPS_PSCSOEO_COMBE MARTIN | 2675 | 2675 | A1 | Storm discharge at pumping station | SS 5775 4719 | GB108051020440 | Umber | RIVER UMBER |  | COMBE MARTIN BEACH | Commissioned pre-2016 - full year data expected | 489.05 | 43 | 100
South West Water | CROWLAS BRIDGE PUMPING STATION | CROWLAS BRIDGE SPS_PSCSOEO_CROWLAS | 301605 | 301605 | A1 | Storm discharge at pumping station | SW 5164 3315 | GB108048002110 | Marazion River | RED RIVER |  |  | Commissioned pre-2016 - full year data expected | 8.46 | 2 | 100
South West Water | CROWNDALE WWTW | CROWNDALE STW_SSO_TAVISTOCK | 301918 | 301918 | A2 | Storm tank at WwTW | SX 4725 7213 | GB108047007840 | Lower River Tavy | RIVER TAVY |  |  | Commissioned in 2018 - full year data expected | 870.24 | 66 | 100 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue
South West Water | CROWNDALE COTTAGES CSO | CROWNDALE_CSO_TAVISTOCK | 301885 | 301885 | A1 | SO on sewer network | SX 4737 7257 | GB108047007840 | Lower River Tavy | TRIB OF THE RIVER TAVY |  |  | Commissioned in 2016 - full year data expected | 347.26 | 76 | 81 | Sensor failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
South West Water | CROWNHILL ROAD CSO | CROWNHILL RD_CSO_PLYMOUTH | 301721 | 301721 | A1 | SO on sewer network | SX 4784 5887 | 73 | #N/A | HONICKNOWLE STREAM VIA SWS |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 100
South West Water | CROWNHILL ROAD CSO | CROWNHILL ROAD_CSO_PLYMOUTH_FOOTPATH | 301706 | 301706 | A1 | SO on sewer network | SX 4784 5886 | 73 | #N/A | HONICKNOWLE STREAM |  |  | Commissioned in 2016 - full year data expected | 43.25 | 18 | 100
South West Water | CROYDE WASTEWATER TREATMENT WORKS | CROYDE SCREENS_PSCSOEO_CROYDE | 201127 | 201127 | A1 | Storm discharge at pumping station | SS 4334 3956 | 235 | #N/A | CROYDE BAY (COASTAL) |  | CROYDE BAY BEACH | Commissioned pre-2016 - full year data expected | 0.58 | 2 | 100
South West Water | CROYDE WASTEWATER TREATMENT WORKS | CROYDE STW_SO_CROYDE | 201127 | 201127 | A2 | Inlet SO at WwTW | SS 4223 4021 | 235 | #N/A | CROYDE BAY (COASTAL) |  |  | Commissioned in 2017 - full year data expected | 56.95 | 14 | 100
South West Water | CULVER ROAD CSO | CULVER ROAD_CSO_SALTASH | 302585 | 302585 | A1 | SO on sewer network | SX 4338 5875 | 71 | #N/A | RIVER TAMAR ESTUARY (E) | Tamar |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | DALE ROAD CSO | DALE ROAD/EAST PARK AVENUE_CSO_PLYMOUTH | 301780 | 301780 | A1 | SO on sewer network | SX 4622 5441 | 73 | #N/A | STONEHOUSE CREEK VIA SWS (EST) |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 35 | Sensor failure / issue | Resolved - November
South West Water | DALWOOD PUMPING STATION | DALWOOD SPST_PSCSOEO_DALWOOD | 203072 | 203072 | A1 | Storm discharge at pumping station | SY 2501 9988 | GB108045009300 | Corry Brook | THE CORRY BROOK (S) |  |  | EDM to be installed by December 2023
South West Water | DANIELS LANE CSO | DANIELS LN_CSO_ST AUSTELL | 032052/SF/01 | 32052 | A1 | SO on sewer network | SX 0355 5253 | GB108048001330 | Crinnis River | SANDY RIVER | St.Austell Bay | SHORTHORN BEACH | Commissioned pre-2016 - full year data expected | 26.25 | 13 | 62 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | DARK STREET LANE CSO | DARK STREET LANE TANK_CSO_PLYMPTON | 301704 | 301704 | A1 | SO on sewer network | SX 5415 5596 | 73 | #N/A | LONGBROOK STREAM |  | PLYMOUTH HOE (EAST) | Commissioned pre-2016 - full year data expected | 19.28 | 26 | 96
South West Water | DARTHAVEN MARINA PUMPING STATION | DARTHAVEN MARINA SPS_PSCSO_KINGSWEAR | 202398 | 202398 | A1 | SO on sewer network | SX 8817 5141 | 23 | #N/A | RIVER DART (ESTUARINE) |  |  | Commissioned in 2016 - full year data expected | 9.15 | 25 | 100
South West Water | DARTINGTON C CSO | DARTINGTON C_CSO_DARTINGTON | 202968 | 202968 | A1 | SO on sewer network | SX 7919 6193 | GB108046005160 | Bidwell Brook | BIDWELL BROOK | Dart |  | Commissioned in 2019 - full year data expected | 414.17 | 44 | 76 | Comms failure / issue | Resolved - April
South West Water | DARTINGTON CLOSE PUMPING STATION | DARTINGTON CLOSE SPS_PSCSOEO_TORRINGTON | 200080 | 200080 | A1 | Storm discharge at pumping station | SS 5024 1974 | GB108050014660 | Torridge (Lew to Estuary) | COMMON LAKE STREAM | Taw/Torridge |  | Commissioned pre-2016 - full year data expected | 6.09 | 8 | 96
South West Water | DARTINGTON B CSO | DARTINGTON SCH TWO_CSO_DARTINGTON | 202963 | 202963 | A1 | SO on sewer network | SX 7870 6219 | GB108046005160 | Bidwell Brook | BIDWELL BROOK | Dart |  | Commissioned in 2017 - full year data expected | 636.91 | 64 | 100
South West Water | DAWES LANE COMBINED SEWER OVERFLOW | DAWS LN_CSO_MILLBROOK | 301859 | 301859 | A1 | SO on sewer network | SX 4246 5220 | 72 | #N/A | MILLBROOK VIA SWS |  |  | Commissioned in 2019 - full year data expected | 1.21 | 8 | 100
South West Water | DELABOLE WASTEWATER TREATMENT WORKS | DELABOLE STW_SO_DELABOLE | NRA-SW-4934 | NRA-SW-4934 | A2 | Inlet SO at WwTW | SX 0729 8294 | GB108049007050 | Allen | RIVER ALLEN |  |  | Commissioned in 2016 - full year data expected | 1719.1 | 247 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
South West Water | DELABOLE WASTEWATER TREATMENT WORKS | DELABOLE STW_SSO_DELABOLE | NRA-SW-4934 | NRA-SW-4934 | A3 | Storm tank at WwTW | SX 0729 8294 | GB108049007050 | Allen | RIVER ALLEN |  |  | Commissioned in 2016 - full year data expected | 2142.33 | 134 | 94 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
South West Water | DERBY ROAD COMBINED SEWER OVERFLOW | DERBY ROAD_CSO_BARNSTAPLE | EPRMB3798AM | EPR/MB3798AM | A1 | SO on sewer network | SS 5609 3369 | 198 | #N/A | TRIB OF RIVER YEO VIA SWS |  |  | EDM to be installed by December 2023
South West Water | HOLSWORTHY (DERRITON) STW | DERRITON STW_SO_HOLSWORTHY | NRA-SW-6975 | NRA-SW-6975/SS/01 | A2 | Inlet SO at WwTW | SS 3402 0322 | GB108047013880 | Deer | COLES STREAM (S) |  |  | Commissioned in 2018 - full year data expected | 272.83 | 76 | 100
South West Water | HOLSWORTHY (DERRITON) STW | DERRITON STW_SSO_HOLSWORTHY | NRA-SW-6975 | NRA-SW-6975/SO/01 | A3 | Storm tank at WwTW | SS 3405 0323 | GB108047013880 | Deer | COLES STREAM (S) |  |  | Commissioned in 2018 - full year data expected | 2673.86 | 135 | 100
South West Water | DEVORAN PUMPING STATION | DEVORAN SPS_PSCSOEO_DEVORAN | 302071 | 302071 | A1 | Storm discharge at pumping station | SW 7913 3927 | GB108048001231 | Lower River Carnon | RIVER CARNON ESTUARY(E) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 35.56 | 3 | 100
South West Water | DIPTFORD SEWAGE TREATMENT WORKS | DIPTFORD STW_SO_DIPTFORD | 200400 | 200400/CS/01 | A2 | Inlet SO at WwTW | SX 7242 5652 | GB108046004940 | Avon - Upper | RIVER AVON | Avon |  | May 2021 | 97.69 | 83 | 100
South West Water | EAST PORTLEMOUTH WWTW | DITCH END S T_PSCSOEO_EAST PORTLEMOUTH | 203866 | 203866 | A1 | Storm discharge at pumping station | SX 7461 3890 | 69 | #N/A | SALCOMBE ESTUARY (ESTUARINE) |  |  | Commissioned in 2016 - full year data expected | 210.38 | 13 | 100
South West Water | DITTISHAM WWTW | DITTISHAM MAIN STW_SO_DITTISHAM | 202711 | 202711 | A2 | Inlet SO at WwTW | SX 8659 5500 | 23 | #N/A | RIVER DART ESTUARY | Dart |  | Commissioned pre-2016 - full year data expected | 164.15 | 44 | 100
South West Water | DIX'S FIELD CSO | DIXS FIELD_CSO_EXETER | EPRDB3493NV | EPR/DB3493NV | A1 | SO on sewer network | SX 9224 9188 | GB108045009040 | Exe (Creedy to Estuary) | RIVER EXE VIA SW SEWER | Exe |  | Commissioned in 2018 - full year data expected | 0 | 0 | 100
South West Water | DOBLES LANE PSCSO/EO | DOBLES LANE SPS_PSCSOEO_HOLSWORTHY | 302098 | 302098/PC/01 | A1 | Storm discharge at pumping station | SS 3430 0472 | GB108047013880 | Deer | TRIB RIVER DEER (S) |  |  | EDM to be installed by December 2023
South West Water | DOBWALLS SPS | DOBWALLS MAIN_CSO_DOBWALLS | NRA-SW-3207 | NRA-SW-3207 | A1 | SO on sewer network | SX 2156 6455 | GB108048002000 | West Looe River | UNNAMED TRIB TO WEST LOOE RIVR |  |  | EDM to be installed by December 2023
South West Water | DOBWALLS SPS | DOBWALLS SPS_PSCSOEO_DOBWALLS | NRA-SW-3206 | NRA-SW-3206 | A1 | Storm discharge at pumping station | SX 2134 6387 | GB108048002000 | West Looe River | UNNAMED TRIB TO WEST LOOE RIVR |  |  | EDM to be installed by December 2023
South West Water | DOCKYARD NO.1 | DOCKYARD No1 SPS_PSCSOEO_PLYMOUTH | 301985 | 301985 | A1 | Storm discharge at pumping station | SX 4460 5589 | 73 | #N/A | RIVER TAMAR (ESTUARINE) |  |  | Commissioned in 2016 - full year data expected | 0.3 | 1 | 100
South West Water | PS-DY2, NORTH YARD, DEVONPORT | DOCKYARD No2 SPS_PSCSOEO_PLYMOUTH | 301986 | 301986 | A1 | Storm discharge at pumping station | SX 4483 5605 | 73 | #N/A | RIVER TAMAR(E) |  |  | Commissioned in 2016 - full year data expected | 2277.17 | 145 | 100
South West Water | DOCKYARD NO.3 PUMPING STATION | DOCKYARD No3 SPS_PSCSOEO_PLYMOUTH | 301993 | 301993 | A1 | Storm discharge at pumping station | SX 4468 5420 | 73 | #N/A | RIVER TAMAR (ESTUARINE) |  |  | Commissioned in 2016 - full year data expected | 490.29 | 57 | 100
South West Water | BEER CAR PARK PUMPING STATION | DOLPHIN ROAD CAR PARK SPS_PSCSOEO_BEER | 202698 | 202698 | A1 | Storm discharge at pumping station | SY 2268 8783 | 407 | #N/A | LYME BAY/SEATON BAY(C) |  | BEER BEACH | Commissioned pre-2016 - full year data expected | 60.52 | 29 | 98
South West Water | DOWNDERRY | DOWNDERRY SPST_PSCSOEO_DOWNDERRY | 037807/PC/01 | 037807/PC/01 | A1 | Storm discharge at pumping station | SX 3203 5370 | 265 | #N/A | ENGLISH CHANNEL |  | DOWNDERRY BEACH | Commissioned pre-2016 - full year data expected | 82.49 | 25 | 100
South West Water | DRAGONS PIT COMBINED SEWER OVERFLOW | DRAGONS PIT_CSO_BODMIN | 301826 | 301826 | A1 | SO on sewer network | SX 0754 6535 | GB108049000040 | St Lawrence Stream | TRIB OF ST LAWRENCE STREAM |  |  | Commissioned in 2018 - full year data expected | 46.43 | 56 | 88 | Comms failure / issue | Resolved - November
South West Water | DRIMPTON PUMPING STATION | DRIMPTON SPST_PSCSOEO_DRIMPTON | 201669 | 201669 | A1 | Storm discharge at pumping station | ST 4164 0516 | GB108045014840 | Upper Axe | TEMPLE BROOK |  |  | Commissioned in 2017 - full year data expected | 249.23 | 23 | 98.56
South West Water | DUKE STREET PUMPING STATION | DUKE STREET SPST_PSCSOEO_CULLOMPTON | 201542 | 201542 | A1 | Storm discharge at pumping station | ST 0238 0673 | GB108045014970 | Lower Culm | CULLOMPTON MILL LEAT |  |  | Commissioned in 2017 - full year data expected | 455.24 | 41 | 100
South West Water | DULFORD PSCSO/EO | DULFORD SPST_PSCSOEO_DULFORD | 201670 | 201670/PC/01 | A1 | Storm discharge at pumping station | ST 0697 0596 | GB108045009110 | Weaver | WEAVER (S) |  |  | EDM to be installed by December 2023
South West Water | DULOE STW | DULOE STW_SO_DULOE | 15/48/173/P/2 | 15/48/173/P/2 | A2 | Inlet SO at WwTW | SX 2305 5823 | GB108048002000 | West Looe River | TRIB OF WEST LOOE RIVER |  |  | EDM to be installed by December 2023
South West Water | DULVERTON WWTW | DULVERTON STW_SO_DULVERTON | 203027 | 203027 | A2 | Inlet SO at WwTW | SS 9158 2728 | GB108045015100 | Lower Barle | RIVER BARLE |  |  | Commissioned in 2018 - full year data expected | 821.92 | 174 | 99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
South West Water | DULVERTON WWTW | DULVERTON STW_SSO_DULVERTON | 203027 | 203027 | A3 | Storm tank at WwTW | SS 9158 2728 | GB108045015100 | Lower Barle | RIVER BARLE |  |  | Commissioned in 2018 - full year data expected | 1569.76 | 92 | 99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP7 or Green Recovery
South West Water | DUNKESWELL PS | DUNKESWELL SPS_PSCSO_DUNKESWELL | 203692 | 203692 | A1 | SO on sewer network | ST 1426 0770 | GB108045014920 | Madford River | DUNKESWELL STREAM(S) |  |  | EDM to be installed by December 2023
South West Water | DUNKESWELL WWTW | DUNKESWELL STW_SO_DUNKESWELL | 203109 | 203109 | A2 | Inlet SO at WwTW | ST 1519 0858 | GB108045014920 | Madford River | RIVER MADFORD |  |  | Commissioned in 2020 - full year data expected | 121.12 | 24 | 66 | Power failure / issue | N/A - Ongoing investigation
South West Water | DUNKESWELL WWTW | DUNKESWELL STW_SSO_DUNKESWELL | 203109 | 203109 | A3 | Storm tank at WwTW | ST 1519 0858 | GB108045014920 | Madford River | RIVER MADFORD |  |  | Commissioned in 2020 - full year data expected | 404.74 | 62 | 98
South West Water | DUNSFORD ROAD CSO | DUNSFORD RD_CSO_EXETER | 201932 | 201932 | A1 | SO on sewer network | SX 9299 9067 | 19 | #N/A | RIVER EXE VIA SWS | Exe |  | Commissioned in 2017 - full year data expected | 61.54 | 44 | 100
South West Water | DUNSFORD WWTW | DUNSFORD STW_SO_TEIGN VALLEY | DRA 1196 | DRA 1196 | A2 | Inlet SO at WwTW | SX 8199 8897 | GB108046008590 | Reedy Brook | RIVER TEIGN & REEDY BROOK |  |  | Commissioned pre-2016 - full year data expected | 3186.16 | 163 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP7 or Green Recovery
South West Water | EAST CHARLETON PUMPING STATION | E CHARLETON SPS_PSCSOEO_EAST CHARLETON | 201660 | 201660 | A1 | Storm discharge at pumping station | SX 7627 4260 | 69 | #N/A | TRIB OF FROGMORE CREEK | Salcombe |  | Commissioned in 2016 - full year data expected | 914.8 | 47 | 99
South West Water | EAST ALLINGTON WWTW | EAST ALLINGTON STW_SSO_EAST ALLINGTON | SWWA 852 | SWWA 852 | A2 | Storm tank at WwTW | SX 7654 4874 | GB108046004870 | Small Bk | SMALL BROOK |  |  | Commissioned in 2019 - full year data expected | 370.18 | 37 | 100
South West Water | EAST BUDLEIGH PUMPING STATION | EAST BUDLEIGH SPS_CSOEO_EAST BUDLEIGH | 201671 | 201671 | A1 | SO on sewer network | SY 0774 8419 | 18 | #N/A | RIVER OTTER |  |  | Commissioned in 2017 - full year data expected | 60.67 | 17 | 100
South West Water | EAST OGWELL WWTW | EAST OGWELL STW_SSO_EAST OGWELL | DRA 239 | DRA 239 | A2 | Storm tank at WwTW | SX 8412 7089 | GB108046008450 | Lemon | RIVER LEMON | Teign |  | Commissioned in 2017 - full year data expected | 1408.85 | 84 | 100
South West Water | GREENACRE PSCSO/EO | EAST STREET A SPS_PSCSOEO_CHULMLEIGH | 201614 | 201614/PC/01 | A1 | Storm discharge at pumping station | SS 6933 1433 | GB108050013960 | Huntacott Water | TRIB LITTLE DART (S) |  |  | EDM to be installed by December 2023
South West Water | EAST STREET PSCSO/EO | EAST STREET A SPS_PSCSOEO_CHULMLEIGH2 | 201615 | 201615/PC/01 | A1 | Storm discharge at pumping station | SS 6933 1433 | GB108050013960 | Huntacott Water | TRIB LITTLE DART RIVER (S) |  |  | EDM to be installed by December 2023
South West Water | EAST STREET CSO | EAST STREET_CSO_NORTH MOLTON | 201948 | 201948/CS/01 | A1 | SO on sewer network | SS 7436 2983 | GB108050019970 | Mole (Source to Burcombe Stream) | R. MOLE (S) |  |  | EDM to be installed by December 2023
South West Water | EAST TAPHOUSE WWTW | EAST TAPHOUSE STW_SO_EAST TAPHOUSE | SWWA 730 | SWWA 730 | A2 | Inlet SO at WwTW | SX 1803 6345 | GB108048001410 | Fowey (Warleggan to St Neot) | TRIBUTARY OF RIVER FOWEY |  |  | Commissioned in 2019 - full year data expected | 31.83 | 25 | 100
South West Water | EAST YARDE SEWAGE TREATMENT WORKS | EAST YARDE STW_SO_MILTON DAMEREL | 201238 | 201238 | A2 | Inlet SO at WwTW | SS 4939 1441 | GB108050014260 | Upper River Mere | TRIBUTARY OF RIVER MERE (S) |  |  | EDM to be installed by December 2023
South West Water | EASTERN KINGS PUMPING STATION | EASTERN KINGS SPS_PSCSO_PLYMOUTH | 300738 | 300738 | A1 | SO on sewer network | SX 4668 5348 | 73 | #N/A | PLYMOUTH SOUND (E) |  | PLYMOUTH HOE (WEST) | Commissioned pre-2016 - full year data expected | 162.09 | 34 | 100
South West Water | EDEN PARK CSO | EDEN PARK_CSO_BRIXHAM | 202704 | 202704 | A1 | SO on sewer network | SX 9217 5532 | 429 | #N/A | HIGHER BRIXHAM STREAM(S) | Brixham |  | Commissioned pre-2016 - full year data expected | 7.8 | 7 | 13 | Comms failure / issue | Resolved - November
South West Water | EDINBURGH STREET (PS5) PS | EDINBURGH STREET PSCSOEO_PLYMOUTH | 301989 | 301989 | A2 | Storm discharge at pumping station | SX 4468 5420 | 73 | #N/A | RIVER TAMAR (ESTUARINE) |  |  | Commissioned in 2016 - full year data expected | 110.07 | 56 | 100
South West Water | EDWARD STREET CSO | EDWARD ST_CSO_TRURO | 302677 | 302677 | A1 | SO on sewer network | SW 8227 4491 | GB108048002340 | Kenwyn | RIVER KENWYN(S) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 13.36 | 9 | 100
South West Water | EFFORD MARSH CSO | EFFORD MARSH_CSO_PLYMOUTH | 301675 | 301675 | A1 | SO on sewer network | SX 5142 5684 | 73 | #N/A | LEIGHAM MILL STREAM |  | PLYMOUTH HOE (EAST) | Commissioned in 2018 - full year data expected | 455.55 | 56 | 85 | Comms failure / issue | Resolved - June
South West Water | EGLOSHAYLE PUMPING STATION | EGLOSHAYLE ROAD SPS_PSCSOEO_WADEBRIDGE | 302976 | 302976 | A1 | Storm discharge at pumping station | SW 9971 7207 | 135 | #N/A | CAMEL ESTUARY (E) | Camel |  | Commissioned pre-2016 - full year data expected | 1.69 | 9 | 100
South West Water | EGLOSKERRY PUMPING STATION | EGLOSKERRY SPS_PSCSOEO_LAUNCESTON | 302100 | 302100 | A1 | Storm discharge at pumping station | SX 2774 8649 | GB108047007981 | Lower River Ottery | TRIBUTARY OF THE RIVER OTTERY |  |  | Commissioned in 2020 - full year data expected | 81.63 | 29 | 100
South West Water | ELBURTON SOUTH PS | ELBURTON SOUTH SPS_PSCSOEO_PLYMOUTH | 303467 | 303467 | A1 | Storm discharge at pumping station | SX 5377 5302 | 70 | #N/A | TRIB OF RIVER YEALM EST (S) | Yealm |  | Commissioned pre-2016 - full year data expected | 19.96 | 5 | 100
South West Water | ELM ROAD COMBINED SEWER OVERFLOW | ELM RD_CSO_NEWTON ABBOT | 201682 | 201682 | A1 | SO on sewer network | SX 8610 7147 | GB108046008450 | Lemon | TRIB OF RIVER TEIGN | Teign |  | Commissioned in 2018 - full year data expected | 26.77 | 18 | 100
South West Water | ELM GROVE CSO | ELMGROVE RD_CSO_DAWLISH | 200825 | 200825/CS/01 | A1 | SO on sewer network | SX 9676 7705 | 20 | #N/A | LYME BAY (C) |  | DAWLISH (TOWN) BEACH | Commissioned pre-2016 - full year data expected | 0.09 | 1 | 49 | Comms failure / issue | Resolved - November
South West Water | EMBANKMENT ROAD PUMPING STATION | EMBANKMENT ROAD_PSCSOEO_PLYMOUTH | 300740 | 300740 | A1 | Storm discharge at pumping station | SX 5000 5465 | 73 | #N/A | RIVER PLYM (ESTUARINE) |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 100
South West Water | ERME ROAD CSO | ERME RD_CSO_IVYBRIDGE | 201862 | 201862 | A1 | SO on sewer network | SX 6360 5624 | GB108046005200 | Erme | RIVER ERM (S) |  | MOTHECOMBE BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | ERMINGTON STW | ERMINGTON STW_SO_ERMINGTON | NRA-SW-1188 | NRA-SW-1188 | A2 | Inlet SO at WwTW | SX 6339 5237 | GB108046005040 | Lower Erme | RIVER ERME |  | MOTHECOMBE BEACH | Commissioned pre-2016 - full year data expected | 103.99 | 10 | 100
South West Water | ERNESETTLE LANE SPORTSGROUND CSO | ERNESETTLE LANE_CSO_PLYMOUTH | 301770 | 301770 | A1 | SO on sewer network | SX 4424 6023 | 73 | #N/A | RIVER TAMAR VIA SWS (E) |  |  | Commissioned in 2018 - full year data expected | 30.73 | 39 | 96
South West Water | ERNESETTLE SEWAGE TREATMENT WORKS | ERNESETTLE STW_SO_PLYMOUTH | 301142 | 301142 | A2 | Inlet SO at WwTW | SX 4424 6023 | 73 | #N/A | RIVER TAMAR (E) | Tamar |  | Commissioned pre-2016 - full year data expected | 481.44 | 74 | 100
South West Water | ERNESETTLE SEWAGE TREATMENT WORKS | ERNESETTLE STW_SSO_PLYMOUTH | 301142 | 301142 | A3 | Storm tank at WwTW | SX 4424 6023 | 73 | #N/A | RIVER TAMAR (E) | Tamar |  | Commissioned pre-2016 - full year data expected | 961.83 | 59 | 100
South West Water | ETHELWYNNE BROWN CLOSE PS | ETHELWYN BROWN ROAD SPS_PSCSOEO_BIDEFORD | 203292 | 203292 | A1 | Storm discharge at pumping station | SS 4534 2665 | 199 | #N/A | RIVER TORRIDGE ESTUARY(E) | Taw/Torridge |  | Commissioned pre-2016 - full year data expected | 10.46 | 11 | 100
South West Water | ETON PLACE CSO | ETON PLACE_CSO_PLYMOUTH | 301779 | 301779 | A1 | SO on sewer network | SX 4697 5400 | 73 | #N/A | MILLBAY DOCK VIA SWS-ESTUARINE |  |  | Commissioned in 2017 - full year data expected | 99.95 | 12 | 100
South West Water | EXE STREET CSO | EXE ST_CSO_EXETER | 201377 | 201377 | A1 | SO on sewer network | SX 9146 9251 | GB108045009040 | Exe (Creedy to Estuary) | HIGHER LEAT | Exe |  | Commissioned in 2017 - full year data expected | 0.49 | 1 | 100
South West Water | EXETER BOWLING CLUB CSO | EXETER BOWLING CLUB_CSO_EXETER | 201922 | 201922 | A1 | SO on sewer network | SX 9223 9189 | GB108045009040 | Exe (Creedy to Estuary) | RIVER EXE VIA SWS | Exe |  | Commissioned in 2018 - full year data expected | 1.06 | 5 | 100
South West Water | EXETER COLLEGE CSO | EXETER COLLEGE ANNEX_CSO_EXETER | 201375 | 201375 | A1 | SO on sewer network | SX 9147 9250 | GB108045009040 | Exe (Creedy to Estuary) | HIGHER LEAT VIA SW SEWER | Exe |  | Commissioned in 2017 - full year data expected | 0 | 0 | 100
South West Water | EXETER ROAD CSO - EXMOUTH | EXETER RD_CSO_EXMOUTH | 200128/CS/01 | 200128/CS/01 | A1 | SO on sewer network | SX 9997 8201 | 19 | #N/A | WITHYCOMBE BROOK | Exe |  | Commissioned pre-2016 - full year data expected | 13.47 | 12 | 22 | Sensor failure / issue | Resolved - January
South West Water | EXETER ROAD PUMPING STATION | EXETER ROAD SPST_PSCSOEO_TIVERTON | 201673 | 201673 | A1 | Storm discharge at pumping station | SS 9492 1164 | GB108045015050 | Exe (Barle to Culm) | COTTEY BROOK |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 73 | Sensor failure / issue | Resolved - January
South West Water | MILBURY LANE PUMPING STATION | EXMINSTER SPST_PSCSOEO_EXMINSTER | 201580 | 201580 | A1 | Storm discharge at pumping station | SX 9483 8797 | 20 | #N/A | TRIB OF THE BERRY BROOK | Exe |  | Commissioned in 2016 - full year data expected | 0.01 | 2 | 100
South West Water | MILBURY LANE PUMPING STATION | EXMINSTER SPST_PSCSOEO_EXMINSTER | 201580 | 201580 | A1 | Storm discharge at pumping station | SX 9500 8834 | 20 | #N/A | TRIB OF THE BERRY BROOK | Exe |  | Commissioned in 2016 - full year data expected | 0.01 | 2 | 100
South West Water | EXTON NORTH PS | EXTON NORTH SPS_PSCSOEO_EXMOUTH | 203229 | 203229 | A1 | Storm discharge at pumping station | SX 9769 8689 | 19 | #N/A | RIVER CLYST (ESTUARINE) | Exe |  | Commissioned in 2016 - full year data expected | 1423.08 | 110 | 100
South West Water | EXTON SOUTH PUMPING STATION | EXTON SOUTH SPS_PSCSOEO_EXMOUTH | 203230 | 203230 | A1 | Storm discharge at pumping station | SX 9809 8624 | 19 | #N/A | WOODBURY BROOK (ESTUARINE) | Exe |  | Commissioned in 2016 - full year data expected | 377.77 | 36 | 100
South West Water | FACTORY HOUSES PUMPING STATION | FACTORY HOUSES MENHENIOT_PSCSEO_LISKEARD | 301539 | 301539 | A1 | Storm discharge at pumping station | SX 2843 6203 | GB108048002320 | Seaton | TRIBUTARY OF THE RIVER SEATON |  | SEATON BEACH (CORNWALL) | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | FAIR VIEW CAR PARK CSO | FAIR VIEW CAR PARK_CSO_PILTON | 002494/CS/01 | 2494 | A1 | SO on sewer network | SS 5554 3371 | 198 | #N/A | RIVER YEO VIA SWS (ESTUARINE) | Taw/Torridge |  | Commissioned in 2019 - full year data expected | 0 | 0 | 100
South West Water | FAIRMANTLE STREET CSO | FAIRMANTLE ST CAR PARK_CSO_TRURO | 302680 | 302680 | A1 | SO on sewer network | SW 8286 4464 | 76 | #N/A | RIVER KENWYN(E) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | #N/A | #N/A | 0 | Comms failure / issue | N/A - Ongoing investigation
South West Water | FALMOUTH STW INLET & STORM PS | FALMOUTH DOCKS SPST_PSCSOEO_FALMOUTH | 302999 | 302999 | A1 | Storm discharge at pumping station | SW 8264 3206 | 402 | #N/A | PENRYN RIVER(E) |  |  | EDM to be installed by December 2023
South West Water | FALMOUTH STW INLET & STORM PS | FALMOUTH STW_SO_FALMOUTH | 302999 | 302999 | A2 | Inlet SO at WwTW | SW 8264 3206 | 402 | #N/A | PENRYN RIVER(E) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 355.25 | 29 | 100
South West Water | FENITON WASTEWATER TREATMENT WORKS | FENITON STW_SO_FENITON | NRA-SW-3706 | NRA-SW-3706 | A2 | Inlet SO at WwTW | SY 1160 9890 | GB108045009170 | Lower River Otter | RIVER OTTER |  |  | Commissioned in 2019 - full year data expected | 3.71 | 3 | 100
South West Water | FENITON WASTEWATER TREATMENT WORKS | FENITON STW_SSO_FENITON | NRA-SW-3706 | NRA-SW-3706 | A3 | Storm tank at WwTW | SY 1160 9890 | GB108045009170 | Lower River Otter | RIVER OTTER |  |  | Commissioned in 2019 - full year data expected | 878.18 | 71 | 100
South West Water | FERN PIT PUMPING STATION | FERNPIT SPS_PSCSOEO_NEWQUAY | 301325 | 301325/PC/01 | A1 | Storm discharge at pumping station | SW 7893 6119 | 197 | #N/A | RIVER GANNEL (S) |  | CRANTOCK BEACH | Commissioned pre-2016 - full year data expected | 57.82 | 46 | 100
South West Water | FERRY BOAT INN PUMPING STATION | FERRY BOAT SPST_PSCSOEO_DITTISHAM | 202713 | 202713 | A1 | Storm discharge at pumping station | SX 8674 5482 | 23 | #N/A | RIVER DART ESTUARY | Dart |  | Commissioned pre-2016 - full year data expected | 36.05 | 44 | 97
South West Water | FERRY ROAD PUMPING STATION | FERRY ROAD SPS_PSCSOEO_EXETER | 201634 | 201634 | A1 | Storm discharge at pumping station | SX 9623 8814 | 19 | #N/A | RIVER EXE | Exe |  | Commissioned in 2017 - full year data expected | 0 | 0 | 93
South West Water | FIELD ADJ COUNCIL HOUSES CSO | FIELD ADJ COUNCIL HSES_CSO_BLACKAWTON | 201809 | 201809 | A1 | SO on sewer network | SX 8061 5085 | GB108046004930 | The Gara | BLACKAWTON STREAM |  |  | Commissioned in 2020 - full year data expected | 1.7 | 4 | 74 | Comms failure / issue | Resolved - November
South West Water | R/O 13 WEST STREET CSO | FIELD ADJ STW_CSO_BAMPTON | 201884 | 201884/CS/01 | A1 | SO on sewer network | SS 9546 2201 | GB108045015070 | Lower Batherm | RIVER BATHERN (S) |  |  | EDM to be installed by December 2023
South West Water | FIELD NEAR WAR MEMORIAL CSO | FIELD NR WAR MEMORIAL_CSO_HGHR NETHERTON | 201770 | 201770 | A1 | SO on sewer network | SX 8919 7136 | 22 | #N/A | TRIBUTARY OF RIVER TEIGN |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 100
South West Water | LAIRA PARK CSO | FIELD O/S 32 LAIRA PARK GDN_CSO_PLYMOUTH | 301776 | 301776 | A1 | SO on sewer network | SX 5041 5531 | 73 | #N/A | RIVER PLYM VIA SWS (ESTUARINE) |  | PLYMOUTH HOE (EAST) | Commissioned in 2018 - full year data expected | 212.13 | 96 | 100
South West Water | FINNS CSO | FINNS_CSO_PENZANCE | 301818 | 301818/CS/01 | A1 | SO on sewer network | SW 4810 3117 | GB108048002100 | Trevaylor Stream | LOCAL STREAM (S) |  | LONG ROCK | Commissioned pre-2016 - full year data expected | 83.43 | 40 | 100
South West Water | FIRLANDS ROAD 1 CSO | FIRLANDS RD 1_CSO_TORQUAY | 201937 | 201937 | A1 | SO on sewer network | SX 9153 6654 | 429 | #N/A | TRIBUTARY OF RIVER FLEET |  |  | Commissioned in 2017 - full year data expected | 1.71 | 4 | 100
South West Water | FIRLANDS ROAD 2 CSO | FIRLANDS RD 2_CSO_TORQUAY | 201936 | 201936 | A1 | SO on sewer network | SX 9153 6654 | 429 | #N/A | TRIBUTARY OF RIVER FLEET |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 100
South West Water | FIRE STATION CSO | FIRST AV (FIRE STATION)_CSO_TEIGNMOUTH | 203088 | 203088 | A1 | SO on sewer network | SX 9328 7330 | 22 | #N/A | BITTON BROOK (S) | Teign |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 68 | Comms failure / issue | Resolved - July
South West Water | FIRST AVENUE SERVICE LANE CSO | FIRST AV/SERVICE LN_CSO_EXETER | 201913 | 201913 | A1 | SO on sewer network | SX 9480 9230 | GB108045009050 | North Brook (East Devon) | NORTH BROOK VIA SWS | Exe |  | Commissioned in 2017 - full year data expected | 1.05 | 5 | 100
South West Water | FLEET WALK NO.1 CSO | FLEET WALK 1_CSO_TORQUAY | 200224 | 200224 | A1 | SO on sewer network | SX 9165 6341 | 429 | #N/A | TORQUAY HARBOUR |  | BEACON COVE BEACH | Commissioned pre-2016 - full year data expected | 40.91 | 25 | 100
South West Water | FLEET WALK NO.2 CSO | FLEET WALK 2_CSO_TORQUAY | 200225 | 200225 | A1 | SO on sewer network | SX 9174 6338 | 429 | #N/A | TORQUAY HARBOUR |  | BEACON COVE BEACH | Commissioned pre-2016 - full year data expected | 46.74 | 31 | 100
South West Water | FLORENCE STREET CSO | FLORENCE STREET_CSO_PLYMOUTH | 302614 | 302614 | A1 | SO on sewer network | SX 4469 5835 | 73 | #N/A | WESTON MILL LAKE(S) | Tamar |  | Commissioned pre-2016 - full year data expected | 13.89 | 25 | 100
South West Water | FLUSHING PUMPING STATION | FLUSHING SPST_PSCSOEO_FALMOUTH | 301915 | 301915/PC/01 | A1 | Storm discharge at pumping station | SW 8093 3355 | 402 | #N/A | PENRYN RIVER (E) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 188.55 | 92 | 100
South West Water | FLUXTON WASTEWATER TREATMENT WORKS | FLUXTON STW_SO_OTTERY ST MARY | SWWA 944 | SWWA 944 | A2 | Inlet SO at WwTW | ST 0890 9256 | GB108045009170 | Lower River Otter | TRIBUTARY OF THE RIVER OTTER |  |  | Commissioned in 2019 - full year data expected | 374.69 | 69 | 100
South West Water | FLUXTON WASTEWATER TREATMENT WORKS | FLUXTON STW_SSO_OTTERY ST MARY | SWWA 944 | SWWA 944 | A3 | Storm tank at WwTW | ST 0890 9256 | GB108045009170 | Lower River Otter | TRIBUTARY OF THE RIVER OTTER |  |  | Commissioned in 2019 - full year data expected | 347.97 | 32 | 100
South West Water | FLY CELLARS PSCSO/EO | FLYCOVE SPS_PSCSOEO_NEWQUAY | 301587 | 301587/PC/01 | A1 | Storm discharge at pumping station | SW 8080 6230 | 231 | #N/A | NEWQUAY BAY (C) |  | TOWAN BEACH NEWQUAY | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | FOLLET ROAD CSO | FOLLET RD_CSO_EXETER | 201636 | 201636/CS/01 | A1 | SO on sewer network | SX 9622 8814 | 19 | #N/A | RIVER EXE (E) | Exe |  | Commissioned pre-2016 - full year data expected | 23.68 | 34 | 100
South West Water | FOLLY GATE WWTW SSO | FOLLY GATE STW_SSO_FOLLY GATE | NRA-SW-1243 | NRA-SW-1243 | A2 | Storm tank at WwTW | SX 5726 9811 | GB108050008110 | Middle River Okement | TRIB OF BECKAMOOR BROOK |  |  | EDM to be installed by December 2023
South West Water | FORD & FAIRY CROSS STW | FORD AND FAIRY CROSS STW_SO_FORD | 203909 | 203909 | A2 | Inlet SO at WwTW | SS 4108 2451 | GB108050014470 | Upper River Yeo (Bideford) | TRIB OF RIVER YEO(S) |  |  | EDM to be installed by December 2023
South West Water | FORDE PARK/TORQUAY ROAD CSO | FORDE PARK/TORQUAY RD_CSO_NEWTON ABBOT | 203098 | 203098 | A1 | SO on sewer network | SX 8703 7069 | GB108046005350 | Aller Brook (Teign) - Lower | S/W SEWER TO ALLER BROOK(S) | Teign |  | Commissioned pre-2016 - full year data expected | 258.57 | 60 | 88 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | TORQUAY ROAD CSO | FORDE PARK_CSO_NEWTON ABBOT | 203344 | 203344 | A1 | SO on sewer network | SX 8703 7069 | GB108046005350 | Aller Brook (Teign) - Lower | ALLER BROOK (S) | Teign |  | Commissioned pre-2016 - full year data expected | 4.74 | 14 | 100
South West Water | FORDE ROAD PSCSO/EO | FORDE ROAD SPS_PSCSOEO_NEWTON ABBOT | 203336 | 203336 | A1 | Storm discharge at pumping station | SX 8725 7170 | 22 | #N/A | RIVER TEIGN VIA S/W SEWER(S) | Teign |  | Commissioned pre-2016 - full year data expected | 102.25 | 20 | 100
South West Water | FORDER NO 2 PSCSO/EO | FORDER No2 SPS_PSCSOEO_SALTASH | 302103 | 302103/PC/01 | A1 | Storm discharge at pumping station | SX 4128 5811 | 71 | #N/A | RIVER LYNER (E) | Tamar |  | Commissioned pre-2016 - full year data expected | 3.14 | 4 | 96
South West Water | FORDER VALLEY ROAD CSO | FORDER VALLEY ROAD_CSO_PLYMOUTH | 301676 | 301676 | A1 | SO on sewer network | SX 5106 5733 | 73 | #N/A | LEIGHAM MILL STREAM |  | PLYMOUTH HOE (EAST) | Commissioned in 2018 - full year data expected | 973.33 | 97 | 100
South West Water | FORE STREET CSO | FORE STREET_CSO_BUDLEIGH SALTERTON | 200117/CS/01 | 200117/CS/01 | A1 | SO on sewer network | SY 0649 8188 | 408 | #N/A | KNOWLE STREAM |  | BUDLEIGH SALTERTON BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | FORGE WAY CAR PARK CSO | FORGE WAY CAR PARK_CSO_CULLOMPTON | 201858 | 201858/CS/01 | A1 | SO on sewer network | ST 0227 0743 | GB108045014970 | Lower Culm | MILL STREAM (S) |  |  | Commissioned in 2019 - full year data expected | 0.47 | 2 | 100
South West Water | FORTESCUE COMBINED SEWER OVERFLOW | FORTESCUE_CSO_SIDMOUTH | 201185 | 201185 | A1 | SO on sewer network | SY 1331 8903 | GB108045009160 | Sid | THE RIVER SID VIA SWS |  |  | Commissioned in 2019 - full year data expected | 48.27 | 23 | 54 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | FOWEY SEWAGE TREATMENT WORKS | FOWEY STW_SSO_FOWEY | 302530 | 302530 | A2 | Storm tank at WwTW | SX 1276 5233 | 26 | #N/A | FOWEY ESTUARY (E) | Fowey | READYMONEY COVE | Commissioned pre-2016 - full year data expected | 1393.87 | 173 | 100
South West Water | FRADDON WASTEWATER TREATEMENT WORKS | FRADDON STW_SO_FRADDON | NRA-SW-5666 | NRA-SW-5666 | A2 | Inlet SO at WwTW | SW 9042 5773 | GB108049000230 | Gannel (Upper) | TRIB OF RIVER GANNEL |  |  | Commissioned in 2019 - full year data expected | 824.75 | 122 | 100
South West Water | FRANCES STREET CSO TRURO | FRANCIS ST_CSO_TRURO | 302668 | 302668 | A1 | SO on sewer network | SW 8221 4492 | GB108048002340 | Kenwyn | RIVER KENWYN(S) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 66 | Sensor failure / issue | Resolved - September
South West Water | FREMINGTON PILL PUMPING STATION | FREMINGTON BRIDGE SPS_CSO_FREMINGTON | 203287 | 203287 | A1 | SO on sewer network | SS 5136 3252 | 198 | #N/A | BICKLETON STREAM(S) | Taw/Torridge |  | Commissioned pre-2016 - full year data expected | 167.16 | 21 | 99
South West Water | FURZEGOOD PUMPING STATION | FURZEGOOD SPS_PSCSOEO_MARLDON | 201665 | 201665 | A1 | Storm discharge at pumping station | SX 8645 6299 | GB108046005430 | Hems - Lower | TRIB OF GATCOMBE BROOK | Dart |  | Commissioned in 2016 - full year data expected | 47.71 | 41 | 100
South West Water | GABBER INJECTOR PUMPING STATION | GABBER INJECTOR SPS_PSCSOEO_WEMBURY | 301615 | 301615 | A1 | Storm discharge at pumping station | SX 5065 4977 | 262 | #N/A | HEY BROOK |  |  | Commissioned in 2018 - full year data expected | 10.6 | 13 | 100
South West Water | GALES HILL PUMPING STATION | GALES HILL LOW SPST_PSCSOEO_TEIGNMOUTH | 203347 | 203347 | A1 | Storm discharge at pumping station | SX 9379 7236 | 22 | #N/A | THE TEIGN ESTUARY (E) | Teign | SHALDON BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 98
South West Water | GALMPTON (HOPE COVE) STW | GALMPTON HOPE COVE STW_SSO_SALCOMBE | 202733 | 202733 | A2 | Storm tank at WwTW | SX 6829 4024 | 266 | #N/A | GALMPTON STREAM(S) |  | HOPE COVE BEACH | Commissioned pre-2016 - full year data expected | 19.53 | 17 | 100
South West Water | GARRICK CLOSE CSO | GARRICK CLOSE_CSO_PLYMOUTH | 301705 | 301705 | A1 | SO on sewer network | SX 4726 5875 | 73 | #N/A | HONICKNOWLE STREAM |  | PLYMOUTH HOE (EAST) | Commissioned in 2017 - full year data expected | 31.2 | 41 | 100
South West Water | GENERALS LANE PUMPING STATION | GENERALS LANE SPST_PSCSOEO_STARCROSS | 202633 | 202633 | A1 | Storm discharge at pumping station | SX 9766 8190 | 20 | #N/A | S/WATER SYSTEM TO EXE ESTUARY | Exe |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | GEORGE NYMPTON WWTW SSO | GEORGE NYMPTON STW_SSO_GEORGE NYMPTON | NRA-SW-1255 | NRA-SW-1255 | A2 | Storm tank at WwTW | SS 7006 2287 | GB108050014110 | Mole (Bray to Yeo) | TRIB OF RIVER MOLE |  |  | EDM to be installed by December 2023
South West Water | GITTISHAM PUMPING STATION | GITTISHAM SPST_PSCSOEO_GITTISHAM | 201142 | 201142 | A1 | Storm discharge at pumping station | SY 1342 9887 | GB108045009170 | Lower River Otter | TRIBUTARY OF RIVER OTTER |  |  | Commissioned in 2019 - full year data expected | 548.81 | 62 | 100
South West Water | GLADSTONE TERRACE NORTH | GLADSTONE TERRACE NORTH_CSO_PENZANCE | 300271 | 300271/CS/01 | A1 | SO on sewer network | SW 4995 3134 | 405 | #N/A | LONGROCK STREAM |  | LONG ROCK | Commissioned pre-2016 - full year data expected | 35.19 | 13 | 100
South West Water | GLEBE FARM PUMPING STATION | GLEBE FARM SPS_PSCSOEO_BUCKERELL | 201641 | 201641 | A1 | Storm discharge at pumping station | ST 1272 0040 | GB108045009170 | Lower River Otter | TRIB OF THE RIVER OTTER |  |  | Commissioned in 2017 - full year data expected | 86.62 | 42 | 100
South West Water | GLENHOLT PUMPING STATION | GLENHOLT SPS_PSCSO_PLYMOUTH | 301592 | 301592 | A1 | SO on sewer network | SX 5088 6104 | GB108047004040 | Lower River Plym | TRIB OF THE RIVER PLYM |  | PLYMOUTH HOE (EAST) | Commissioned in 2016 - full year data expected | 726.4 | 73 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: Cost beneficial outcome not yet determined
South West Water | CSO ADJ GLENVIEW | GLENVIEW_CSO_YELVERTON | 300963 | 300963/CS/01 | A1 | SO on sewer network | SX 5261 6568 | GB108047003660 | Meavy | RIVER MEAVY (S) |  |  | EDM to be installed by December 2023
South West Water | GOLANT PUMPING STATION | GOLANT SPST_PSCSOEO_GOLANT | 303327 | 303327 | A1 | Storm discharge at pumping station | SX 1240 5469 | 26 | #N/A | RIVER FOWEY ESTUARY (E) | Fowey |  | Commissioned pre-2016 - full year data expected | 36.75 | 158 | 100
South West Water | GOLBERDON STW | GOLBERDON STW_SO_GOLBERDON | SWWA 2106 | SWWA 2106 | A2 | Inlet SO at WwTW | SX 3197 7092 | GB108047007670 | Lower River Lynher | RIVER LYNHER |  |  | Commissioned in 2018 - full year data expected | 2327.36 | 168 | 100
South West Water | GOLD STREET CSO | GOLD STREET_CSO_TIVERTON | 201819 | 201819 | A1 | SO on sewer network | SS 9576 1256 | GB108045015030 | Lowman | RIVER LOWMAN |  |  | Commissioned in 2017 - full year data expected | 2.3 | 10 | 100
South West Water | GOLDSITHNEY PSCSO/EO | GOLDSITHNEY SPS_PSCSOEO_GOLDSITHNEY | 301606 | 301606/PC/01 | A1 | Storm discharge at pumping station | SW 5417 3084 | GB108048002110 | Marazion River | STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | CHULMLEIGH (GOLF COURSE) | GOLF COURSE_CSO_CHULMLEIGH | 203146 | 203146 | A1 | SO on sewer network | SS 6843 1413 | GB108050014340 | Lower Little River Dart | LITTLE DART RIVER (S) |  |  | EDM to be installed by December 2023
South West Water | GOODLEIGH WWTW | GOODLEIGH STW_SO_GOODLEIGH | 200356 | 200356 | A2 | Inlet SO at WwTW | SS 5982 3394 | GB108050019980 | Coney Gut | GOODLEIGH STREAM |  |  | Commissioned in 2017 - full year data expected | 14.1 | 17 | 100
South West Water | GOONMARRIS PSCSO/EO | GOONAMARRIS_CSO_NANPEAN | 301582 | 301582/CS/01 | A1 | SO on sewer network | SW 9564 5506 | GB108048001350 | Gwindra Stream | GWINDRA STREAM(S) |  |  | EDM to be installed by December 2023
South West Water | GOONHAVERN WWTW | GOONHAVERN STW_SO_GOONHAVERN | NRA-SW-3701 | NRA-SW-3701 | A2 | Inlet SO at WwTW | SW 7772 5298 | GB108049000700 | Bolingey Stream | TRIB OF THE BOLINGEY STREAM |  |  | Commissioned in 2020 - full year data expected | 577.38 | 62 | 100
South West Water | GOONHAVERN WWTW | GOONHAVERN STW_SSO_GOONHAVERN | NRA-SW-3701 | NRA-SW-3701 | A3 | Storm tank at WwTW | SW 7772 5298 | GB108049000700 | Bolingey Stream | TRIB OF THE BOLINGEY STREAM |  |  | Commissioned in 2020 - full year data expected | 1584.93 | 95 | 100
South West Water | GORRAN CHURCHTOWN STW | GORRAN CHURCHTOWN SPST_PSCSOEO_GORRAN | 303580 | 303580 | A1 | Storm discharge at pumping station | SX 0012 4245 | 256 | #N/A | PORTMELLON STREAM(S) |  |  | October 2021 | 22.91 | 6 | 100
South West Water | GORRAN HAVEN PSCSO/EO | GORRAN HAVEN SPST_PSCSOEO_GORRAN HAVEN | 302104 | 302104/PC/01 | A1 | Storm discharge at pumping station | SX 0152 4146 | 256 | #N/A | ATLANTIC OCEAN (C) |  | GORRAN HAVEN (LITTLE PERHAVER) BEACH | Commissioned pre-2016 - full year data expected | 270.94 | 49 | 100
South West Water | GOSLINGS BRIDGE CSO | GOSLINGS BRIDGE_CSO_LYME REGIS | 003957/CS/01 | 003957/CS/01 | A1 | SO on sewer network | SY 3411 9232 | GB108044009760 | Lim | RIVER LIM(S) |  | LYME REGIS CHURCH CLIFF BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 86 | Power failure/ issue | Resolved - October
South West Water | GRAMPOUND PLAYING FIELD CSO | GRAMPOUND NO 2_CSO_GRAMPOUND | NRA-SW-6729 | NRA-SW-6729 | A1 | SO on sewer network | SW 9329 4837 | GB108048001270 | Lower River Fal | RIVER FAL |  |  | EDM to be installed by December 2023
South West Water | GRAMPOUND PLAYING FIELD CSO | Grampound No1_CSO_Grampound | NRA-SW-6729 | NRA-SW-6729 | A1 | SO on sewer network | SW 9329 4837 | GB108048001270 | Lower River Fal | RIVER FAL |  |  | EDM to be installed by December 2023
South West Water | GRAMPOUND ROAD PUMPING STATION | GRAMPOUND ROAD SPST_PSCSOEO_GRAMPOUND | 301655 | 301655 | A1 | Storm discharge at pumping station | SW 9361 5013 | GB108048001270 | Lower River Fal | RIVER FAL |  |  | Commissioned in 2018 - full year data expected | 2073.73 | 136 | 100
South West Water | GRAMPOUND PUMPING STATION | GRAMPOUND SPS_PSCSOEO_GRAMPOUND | 301609 | 301609 | A1 | Storm discharge at pumping station | SW 9329 4838 | GB108048001270 | Lower River Fal | RIVER FAL |  |  | Commissioned in 2018 - full year data expected | 354.95 | 67 | 100
South West Water | GRANARY LANE CSO | GRANARY LANE GAS_CSO_BUDLEIGH SALTERTON | 201689 | 201689/CS/01 | A1 | SO on sewer network | SY 0718 8227 | 18 | #N/A | TRIB OF RIVER OTTER (S) |  | BUDLEIGH SALTERTON BEACH | Commissioned pre-2016 - full year data expected | 20.24 | 16 | 85 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | GRANARY LANE (NORTH) CSO | GRANARY LN_CSO_BUDLEIGH SALTERTON | 200115 | 200115 | A1 | SO on sewer network | SY 0711 8274 | 18 | #N/A | KERSBROOK CHANNEL |  | BUDLEIGH SALTERTON BEACH | Commissioned pre-2016 - full year data expected | 1.04 | 6 | 100
South West Water | TORBAY (BROKENBURY) STW INLET PS/ | GRANGE COURT SPS_PSCSOEO_PAIGNTON | 201073 | 201073 | A1 | Storm discharge at pumping station | SX 8895 5911 | 429 | #N/A | CLENNON VALLEY WATERCOURSE |  | GOODRINGTON BEACH | Commissioned pre-2016 - full year data expected | 0.79 | 4 | 96
South West Water | GRANGE ROAD CSO | GRANGE RD S.A. TANK_CSO_HELSTON | 033997/CS/01 | 33997 | A1 | SO on sewer network | SW 6553 2731 | GB108048001172 | Lower River Cober | RIVER COBER (VIA SWS) |  |  | Commissioned in 2016 - full year data expected | 1.65 | 5 | 100
South West Water | GRATTON WASTEWATER TREATMENT WORKS | GRATTON STW_SSO_YELVERTON | 302125 | 302125 | A2 | Storm tank at WwTW | SX 5234 6670 | GB108047003660 | Meavy | RIVER MEAVY |  |  | Commissioned in 2018 - full year data expected | 2006.92 | 120 | 100
South West Water | GRATTON CSO | GRATTON_CSO_YELVERTON | 301897 | 301897 | A1 | SO on sewer network | SX 5281 6701 | GB108047003660 | Meavy | RIVER MEAVY |  |  | Commissioned in 2020 - full year data expected | 1923.97 | 177 | 100
South West Water | GREENACRES CSO | GREENACRES_CSO_CHAGFORD | 201800 | 201800 | A1 | SO on sewer network | SX 6966 8748 | GB108046008550 | Teign (Upper) | TRIB OF THE RIVER TEIGN |  |  | Commissioned in 2018 - full year data expected | 260.64 | 89 | 70 | Capital / maintenance works affect EDM operation | Resolved - April
South West Water | CSO AT DUNSTANVILLE TERRACE | GREENBANK GARDENS_CSO_FALMOUTH | 303013 | 303013 | A1 | SO on sewer network | SW 8054 3343 | 402 | #N/A | PENRYN RIVER(E) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 90.04 | 34 | 100
South West Water | GROVE PLACE NO.1 CSO | GROVE PLACE NO. 1_CSO_FALMOUTH | 303019 | 303019 | A1 | SO on sewer network | SW 8131 3245 | 402 | #N/A | PENRYN RIVER(E) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 22.04 | 13 | 100
South West Water | REAR OF 12 PENDREA CLOSE CSO | GULVAL PENDREA CLOSE_CSO_PENZANCE | 301819 | 301819/CS/01 | A1 | SO on sewer network | SW 4791 3145 | GB108048002100 | Trevaylor Stream | LOCAL STREAM (S) |  | LONG ROCK |  | #N/A | #N/A | #N/A
South West Water | OUTSIDE 5 TREVARRACK LANE CSO | GULVAL TREVARRACK LANE_CSO_PENZANCE | 301820 | 301820/CS/01 | A1 | SO on sewer network | SW 4792 3151 | GB108048002100 | Trevaylor Stream | LOCAL STREAM (S) |  | LONG ROCK | Commissioned pre-2016 - full year data expected | 542.08 | 116 | 92
South West Water | GUN CLIFF PSEO/CSO | GUN CLIFF SPST_PSCSOEO_LYME REGIS | 200061/PC/01 | 200061/PC/01 | A1 | Storm discharge at pumping station | SY 3426 9207 | GB108044009760 | Lim | RIVER LIM |  | LYME REGIS CHURCH CLIFF BEACH | Commissioned pre-2016 - full year data expected | 72.89 | 10 | 100
South West Water | GUNNISLAKE NO.1 CSO | GUNNISLAKE NO. 1_CSO_GUNNISLAKE | 301844 | 301844/CS/01 | A1 | SO on sewer network | SX 4335 7185 | GB108047007860 | Lower River Tamar | RIVER TAMAR (S) |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 96
South West Water | GUNNISLAKE NO.2 CSO | GUNNISLAKE NO. 2_CSO_GUNNISLAKE | 301845 | 301845 | A1 | SO on sewer network | SX 4335 7185 | GB108047007860 | Lower River Tamar | RIVER TAMAR VIA SWS |  |  | Commissioned in 2020 - full year data expected | 996.74 | 103 | 92
South West Water | GUNNISLAKE WWTW | GUNNISLAKE STW_SO_GUNNISLAKE | SWWA 2413 | SWWA 2413 | A2 | Inlet SO at WwTW | SX 4343 7067 | 71 | #N/A | RIVER TAMAR (ESTUARINE) |  |  | Commissioned in 2019 - full year data expected | 179.83 | 53 | 99
South West Water | GUNNISLAKE WWTW | GUNNISLAKE STW_SSO_GUNNISLAKE | SWWA 2413 | SWWA 2413 | A3 | Storm tank at WwTW | SX 4343 7067 | 71 | #N/A | RIVER TAMAR (ESTUARINE) |  |  | Commissioned in 2019 - full year data expected | 1690.36 | 100 | 100
South West Water | GUSTI VEOR COMBINED SEWER OVERFLOW | GUSTI VEOR_CSO_NEWQUAY | 301321 | 301321/CS/01 | A1 | SO on sewer network | SW 8335 6153 | 197 | #N/A | UNNAMED DITCH,TRENANCE LAKE(S) |  | CRANTOCK BEACH | Commissioned pre-2016 - full year data expected | 19.89 | 33 | 100
South West Water | GWENNAP WASTEWATER TREATMENT WORKS | GWENNAP STW_SO_LANNER ST DAY | NRA-SW-5475 | NRA-SW-5475 | A2 | Inlet SO at WwTW | SW 7485 4039 | GB108048001150 | Hicks Mill Stream | HICKS MILL STREAM |  |  | Commissioned in 2020 - full year data expected | 23.78 | 18 | 100
South West Water | GWENNAP WASTEWATER TREATMENT WORKS | GWENNAP STW_SSO_LANNER ST DAY | NRA-SW-5475 | NRA-SW-5475 | A3 | Storm tank at WwTW | SW 7485 4039 | GB108048001150 | Hicks Mill Stream | HICKS MILL STREAM |  |  | Commissioned in 2020 - full year data expected | 2096.18 | 108 | 96
South West Water | GWINDRA ROAD CSO | GWINDRA_CSO_ST STEPHEN | 301882 | 301882/CS/01 | A1 | SO on sewer network | SW 9487 5313 | GB108048001350 | Gwindra Stream | LAPPA VALLEY (S) |  |  | EDM to be installed by December 2023
South West Water | GWYN ROAD COMBINED SEWER OVERFLOW | GWYN ROAD_CSO_PLYMOUTH | 301733 | 301733 | A1 | SO on sewer network | SX 5015 5478 | 73 | #N/A | RIVER PLYM (ESTUARINE) |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 64 | Comms failure / issue | Resolved - June
South West Water | HACKNEY PS | HACKNEY LANE SPST_PSCSOEO_KINGSTEIGNTON | 203337 | 203337 | A1 | Storm discharge at pumping station | SX 8744 7223 | 22 | #N/A | TRIB OF R.TEIGN(S) | Teign |  | Commissioned pre-2016 - full year data expected | 22.71 | 4 | 100
South West Water | HAM LANE CSO | HAM LN_CSO_WOODBURY | 201815 | 201815 | A1 | SO on sewer network | SY 0074 8693 | GB108045008980 | Polly Brook | WOODBURY BROOK | Exe |  | Commissioned in 2017 - full year data expected | 130.1 | 56 | 100
South West Water | HAM WOODS HAM LANE CSO | HAM WOODS HAM LANE_CSO_PLYMOUTH | 301727 | 301727 | A1 | SO on sewer network | SX 4644 5784 | 73 | #N/A | HAM BROOK |  |  | Commissioned pre-2016 - full year data expected | 518.63 | 27 | 87 | Sensor failure / issue | Resolved - November
South West Water | HANNAFORE PUMPING STATION | HANNAFORE SPS_PSCSOEO_LOOE | 300970 | 300970 | A1 | Storm discharge at pumping station | SX 2554 5212 | 265 | #N/A | LOOE BAY |  | EAST LOOE BEACH | Commissioned pre-2016 - full year data expected | 153.7 | 65 | 100
South West Water | HARBERTON WWTW | HARBERTON STW_SO_HARBERTON | NRA-SW-5295 | NRA-SW-5295 | A2 | Inlet SO at WwTW | SX 7772 5830 | GB108046005170 | Harbourne River | HARBETON STREAM |  |  | Commissioned in 2019 - full year data expected | 2225.09 | 158 | 100
South West Water | HARBERTON WWTW | HARBERTON STW_SSO_HARBERTON | NRA-SW-5295 | NRA-SW-5295 | A3 | Storm tank at WwTW | SX 7772 5830 | GB108046005170 | Harbourne River | HARBETON STREAM |  |  | Commissioned in 2019 - full year data expected | 2635.24 | 166 | 100
South West Water | HARBERTONFORD WWTW | HARBERTONFORD STW_SO_HARBERTONFORD | 203562 | 203562 | A2 | Inlet SO at WwTW | SX 7915 5597 | GB108046005170 | Harbourne River | HARBOURNE RIVER |  |  | Commissioned in 2019 - full year data expected | 2229.52 | 109 | 96
South West Water | LARKSTONE LANE STORM TANK CSO | HARBOUR LARKSTONE LN_CSO_ILFRACOMBE | 203644 | 203644 | A1 | SO on sewer network | SS 5257 4769 | 237 | #N/A | ILFRACOMBE HARBOUR(C) |  | ILFRACOMBE WILDERSMOUTH BEACH | Commissioned pre-2016 - full year data expected | 1833.28 | 100 | 100
South West Water | HARBOUR LIGHTS CSO | HARBOUR LIGHTS_CSO_PORTHILLY | 301863 | 301863/CS/01 | A1 | SO on sewer network | SW 9338 7524 | 135 | #N/A | RIVER CAMEL (S) |  | ROCK BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | PAR NO2 PUMPING STATION | HARBOUR ROAD NO2 SPS_PSCSOEO_PAR | 031750/PC/01 | 31750 | A1 | Storm discharge at pumping station | SX 0762 5336 | GB108048002290 | Par River (Lower) | RIVER PAR | St.Austell Bay | PAR SANDS | Commissioned pre-2016 - full year data expected | 0.82 | 2 | 100
South West Water | HARBOUR ROAD SPS (SEATON) | HARBOUR ROAD SPS_PSCSOEO_SEATON | SWWA 248 | SWWA 248 | A1 | Storm discharge at pumping station | SY 2532 9024 | 17 | #N/A | RIVER AXE ESTUARY |  | SEATON BEACH | Commissioned pre-2016 - full year data expected | 29.26 | 20 | 100
South West Water | PORTHLEVEN HARBOUR ATTENUATION | HARBOUR SPS_PSCSOEO_PORTHLEVEN | 033473/PC/01 | 033473/PC/01 | A1 | Storm discharge at pumping station | SW 6272 2539 | 269 | #N/A | MOUNTS BAY |  | PORTHLEVEN SANDS | Commissioned pre-2016 - full year data expected | 13.33 | 11 | 100
South West Water | HAREWOOD ROAD CSO | HAREWOOD RD_CSO_CALSTOCK | 301833 | 301833 | A1 | SO on sewer network | SX 4363 6844 | 71 | #N/A | RIVER TAMAR (ESTUARINE) |  |  | Commissioned in 2019 - full year data expected | 1000.87 | 175 | 69 | Sensor failure / issue | Resolved - June
South West Water | 45 CRAVEN AVENUE CSO | HARLECH CLOSE_CSO_PLYMOUTH | 301771 | 301711 | A1 | SO on sewer network | SX 4905 5735 | 73 | #N/A | RIVER PLYM VIA SWS (ESTUARINE) |  | PLYMOUTH HOE (EAST) | Commissioned in 2018 - full year data expected | 3.83 | 9 | 100
South West Water | WWTW HARROWBARRO | HARROW BARROW STW_SO_CALLINGTON | NRA-SW-0227 | NRA-SW-0227 | A2 | Inlet SO at WwTW | SX 4029 6973 | GB108047004070 | Cotehele Stream | (S)UNNAMED TRIB RIVER TAMAR |  |  | Commissioned in 2019 - full year data expected | 289.52 | 50 | 68 | Sensor failure / issue | Resolved - June
South West Water | HARROWBEER CSO | HARROWBEER_CSO_YELVERTON | 301898 | 301898/CS/01 | A1 | SO on sewer network | SX 5189 6850 | GB108047007870 | Walkham | RIVER TAVY (S) |  |  | EDM to be installed by December 2023
South West Water | HARTLAND PSCSO/EO | HARTLAND SPS_PSCSOEO_HARTLAND | 201647 | 201647/PC/01 | A1 | Storm discharge at pumping station | SS 2580 2440 | GB108050014050 | Abbey River | RIVER ABBY (S) |  |  | EDM to be installed by December 2023
South West Water | HARTOPP ROAD CSO | HARTOP ROAD_PSCSOEO_EXMOUTH | 200122/CS/01 | 200122/CS/01 | A1 | Storm discharge at pumping station | SX 9996 8146 | 19 | #N/A | EXE ESTUARY | Exe | EXMOUTH BEACH | Commissioned pre-2016 - full year data expected | 118.9 | 50 | 100
South West Water | HATHERLEIGH BRIDGE CSO | HATHERLEIGH BRIDGE_CSO_HATHERLEIGH | 201773 | 201773 | A1 | SO on sewer network | SS 5406 0421 | GB108050008220 | Lower River Lew (Torridge) | RIVER LEW |  |  | Commissioned in 2017 - full year data expected | 335.65 | 96 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: Cost beneficial outcome not yet determined
South West Water | HATT WASTEWATER TREATMENT WORKS | HATT STW_SSO_HATT | NRA-SW-0007 | NRA-SW-0007 | A2 | Storm tank at WwTW | SX 3834 6135 | GB108047007670 | Lower River Lynher | RIVER LYNHER |  |  | Commissioned in 2018 - full year data expected | 864.63 | 63 | 97
South West Water | HAWKINGS WAY CREDITION CSO | HAWKINS WAY CREDITON_CSO_CREDITON | 201867 | 201867 | A1 | SO on sewer network | SS 8448 0041 | GB108045009090 | Middle Creedy | TRIB OF RIVER CREEDY VIA SWS |  |  | Commissioned in 2018 - full year data expected | 7.13 | 16 | 62 | Sensor failure / issue | Resolved - November
South West Water | HAYE ROAD COMBINED SEWER OVERFLOW | HAYE ROAD_CSO_CALLINGTON | 303530 | 303530 | A1 | SO on sewer network | SX 3501 6989 | GB108047007670 | Lower River Lynher | HAYE VALLEY STREAM |  |  | Commissioned in 2019 - full year data expected | 142.66 | 60 | 70 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | HAYES BARN CSO | HAYES BARN EXBOURNE_CSO_EXBOURNE | 201781 | 201781/CS/01 | A1 | SO on sewer network | SS 6042 0217 | GB108050014090 | Hole Brook | HOLEBROOK (S) |  |  | EDM to be installed by December 2023
South West Water | HAYESEND FARM CSO | HAYES END FARM_CSO_PLYMOUTH | 302930 | 302930 | A1 | SO on sewer network | SX 4788 6139 | 73 | #N/A | TRIBUTARY OF TAMERTON STREAM() | Tamar |  | Commissioned pre-2016 - full year data expected | 80.3 | 20 | 77 | Comms failure / issue | Resolved - May
South West Water | HAYLE SEWAGE TREATMENT WORKS | HAYLE STW_SSO_HAYLE | NRA-SW-0782 | NRA-SW-0782 | A2 | Storm tank at WwTW | SW 5593 4326 | 229 | #N/A | ATLANTIC (C) |  | PORTH KIDNEY SANDS | Commissioned pre-2016 - full year data expected | 426.08 | 45 | 56 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | HEATHER PARK PUMPING STATION | HEATHER PARK_PSCSOEO_SOUTH BRENT | 202167 | 202167 | A1 | Storm discharge at pumping station | SX 7051 6016 | GB108046004940 | Avon - Upper | TRIB OF HORSE BROOK VIA SWS | Avon |  | Commissioned in 2016 - full year data expected | 0 | 0 | 100
South West Water | HEATHFIELD ROAD CSO | HEATHFIELD RD_CSO_PLYMOUTH | 301728 | 301728 | A1 | SO on sewer network | SX 5016 5478 | 73 | #N/A | RIVER PLYM (ESTUARINE) |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 81 | Sensor failure / issue | Resolved - July
South West Water | HEATHFIELD STW | HEATHFIELD STW_SSO_NEWTON ABBOT | 203812 | 203812 | A2 | Storm tank at WwTW | SX 8384 7640 | GB108046008470 | Lower Bovey | RIVER BOVEY(S) | Teign |  | Commissioned pre-2016 - full year data expected | 1578.74 | 88 | 100
South West Water | HEAVITREE PLEASURE GROUND CSO | HEAVITREE PLEASURE GROUND_CSO_EXETER | 201908 | 201908 | A1 | SO on sewer network | SX 9479 9229 | GB108045009050 | North Brook (East Devon) | NORTH BROOK VIA SWS | Exe |  | Commissioned in 2017 - full year data expected | 1.53 | 9 | 100
South West Water | IL'CMBE RESEWERAGE- HELE BEACH TANK | HELE BAY SPS_PSCSOEO_ILFRACOMBE | 004365/PC/01 | 004365/PC/01 | A1 | Storm discharge at pumping station | SS 5370 4809 | 237 | #N/A | HELE BAY - BRISTOL CHANNEL |  | ILFRACOMBE (HELE) BEACH | Commissioned pre-2016 - full year data expected | 152.32 | 37 | 100
South West Water | HELEBRIDGE WWTW | HELEBRIDGE STW_SO_BUDE | 301299 | 301299 | A2 | Inlet SO at WwTW | SS 1891 0639 | 234 | #N/A | BUDE BAY (ATLANTIC OCEAN) |  |  | Commissioned in 2019 - full year data expected | 252.64 | 78 | 100
South West Water | HELEBRIDGE WWTW | HELEBRIDGE STW_SSO_BUDE | 301299 | 301299 | A3 | Storm tank at WwTW | SS 1891 0639 | 234 | #N/A | BUDE BAY (ATLANTIC OCEAN) |  |  | Commissioned in 2019 - full year data expected | 213.75 | 38 | 85 | Capital / maintenance works affect EDM operation | Resolved - September
South West Water | HELLARCHER PUMPING STATION | HELLARCHER SPS_PSCSOEO_THE LIZARD | 301599 | 301599 | A1 | Storm discharge at pumping station | SW 6944 1244 | 269 | #N/A | ENGLISH CHANNEL (COASTAL) |  |  | Commissioned in 2018 - full year data expected | 111.19 | 58 | 100
South West Water | HELSTON MARKET PUMPING STATION | HELSTON MARKET SPST_PSCSOEO_HELSTON | 302105 | 302105 | A1 | Storm discharge at pumping station | SW 6554 2736 | GB108048001172 | Lower River Cober | RIVER COBER |  |  | Commissioned in 2018 - full year data expected | 10.1 | 5 | 100
South West Water | HELSTON WWTW | HELSTON STW_SSO_HELSTON | 302822 | 302822 | A2 | Storm tank at WwTW | SW 6530 2683 | GB108048001172 | Lower River Cober | RIVER COBER |  |  | Commissioned in 2017 - full year data expected | 114.31 | 17 | 100
South West Water | HEMYOCK PSCSO/EO | HEMYOCK SPST_PSCSOEO_HEMYOCK | 201633 | 201633/PC/01 | A1 | Storm discharge at pumping station | ST 1384 1393 | GB108045014980 | Middle Culm | RIVER CULM (S) |  |  | EDM to be installed by December 2023
South West Water | HENDRA ROAD CSO | HENDRA RD_CSO_TRURO | 302678 | 302678 | A1 | SO on sewer network | SW 8203 4503 | GB108048002340 | Kenwyn | RIVER KENWYN(S) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 3.49 | 22 | 100
South West Water | CHERITON BISHOP PSCSO/EO | HESCANE SPS_PSCSOEO_CHERITON BISHOP | 202162 | 202162/PC/01 | A1 | Storm discharge at pumping station | SX 7730 9300 | GB108046008600 | Scotley Brook | FORD BROOK (S) |  |  | EDM to be installed by December 2023
South West Water | HEYBROOK BAY PUMPING STATION | HEYBROOK BAY_PSCSOEO_WEMBURY | 301618 | 301618 | A1 | Storm discharge at pumping station | SX 4961 4870 | 262 | #N/A | ENGLISH CHANNEL- HEYBROOK BAY |  |  | Commissioned in 2018 - full year data expected | 121.71 | 61 | 94
South West Water | CSO IN HIGH STREET | HIGH ST_CSO_FALMOUTH | 303014 | 303014 | A1 | SO on sewer network | SW 8083 3302 | 402 | #N/A | PENRYN RIVER(E) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | 191 HIGH STREET CSO | HIGH STREET_CSO_HONITON | 201849 | 201849/CS/01 | A1 | SO on sewer network | ST 1595 0054 | GB108045009180 | Middle River Otter | THE GISSAGE (S) |  |  | EDM to be installed by December 2023
South West Water | HIGHAMPTON WASTEWATER TRTMENT WORKS | HIGHAMPTON STW_SSO_HATHERLEIGH | 200411 | 200411 | A2 | Storm tank at WwTW | SS 4851 0385 | GB108050008230 | Pulworthy Brook | TRIB OF PULWORTHY BROOK (S) |  |  | EDM to be installed by December 2023
South West Water | HIGHER CLOVELLY WWTW | HIGHER CLOVELLY STW_SO_CLOVELLY CROSS | DRA 1518 | DRA 1518 | A2 | Inlet SO at WwTW | SS 3076 2520 | 236 | #N/A | STREAM TO MOUTHMILL BEACH |  |  | EDM to be installed by December 2023
South West Water | HIGH MARSH PSEO (HALF MOON VILLAGE) | HIGHER MARSH SPST_PSCSOEO_NEWTON ST CYRE | 202748 | 202748 | A1 | Storm discharge at pumping station | SX 8967 9746 | GB108045009070 | Lower Creedy | RIVER CREEDY(S) |  |  | EDM to be installed by December 2023
South West Water | HIGHER NETHERTON SPS | HIGHER NETHERTON SPS_PSCSOEO_NETHERTON | 002660/PC/01 | 002660/PC/01 | A1 | Storm discharge at pumping station | SX 8919 7136 | 22 | #N/A | NETHERTON BROOK | Teign |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | OPP 65 HIGHWEEK ROAD CSO | HIGHWEEK RD_CSO_NEWTON ABBOT | 203338 | 203338 | A1 | SO on sewer network | SX 8574 7132 | GB108046008450 | Lemon | RIVER LEMON(S) | Teign |  | Commissioned pre-2016 - full year data expected | 27.31 | 6 | 95
South West Water | BRUNSWICK HOUSE CSO | HIGHWEEK SYPHON INLET_CSO_NEWTON ABBOT | 203099 | 203099 | A1 | SO on sewer network | SX 8588 7140 | GB108046008450 | Lemon | THE RIVER LEMON (S) | Teign |  | Commissioned pre-2016 - full year data expected | 0.19 | 2 | 100
South West Water | OKEHAMPTON STW | HILL BARTON STW_SO_OKEHAMPTON | 202463 | 202463 | A2 | Inlet SO at WwTW | SX 5987 9826 | GB108050008110 | Middle River Okement | RIVER OKEMENT(S) |  |  | Commissioned in 2016 - full year data expected | 173.8 | 62 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: Cost beneficial outcome not yet determined
South West Water | OKEHAMPTON STW | HILL BARTON STW_SSO_OKEHAMPTON | 202463 | 202463 | A3 | Storm tank at WwTW | SX 6004 9825 | GB108050008110 | Middle River Okement | RIVER OKEMENT(S) |  |  | Commissioned in 2016 - full year data expected | 963.43 | 80 | 100 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | N/A - Operational solution applied
South West Water | HMS CAMBRIDGE PUMPING STATION | HMS CAMBRIDGE SPS_PSCSOEO_WEMBURY | 301619 | 301619 | A1 | Storm discharge at pumping station | SX 5047 4835 | 262 | #N/A | ENGLISH CHANNELAT WEMBURY BAY |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 100
South West Water | HOLBETON SEWAGE TREATMENT WORKS | HOLBETON STW_SO_HOLBETON | 202650 | 202650 | A2 | Inlet SO at WwTW | SX 6200 5021 | 25 | #N/A | RIVER ERME(E) |  | MOTHECOMBE BEACH | Commissioned pre-2016 - full year data expected | 68.44 | 44 | 76 | Power failure/ issue | Resolved - September
South West Water | HOLBETON SEWAGE TREATMENT WORKS | HOLBETON STW_SSO_HOLBETON | 202650 | 202650 | A3 | Storm tank at WwTW | SX 6246 4979 | 25 | #N/A | RIVER ERME(E) |  | MOTHECOMBE BEACH | Commissioned pre-2016 - full year data expected | 529.27 | 80 | 73 | Sensor failure / issue | Resolved - May
South West Water | HOLCOMBE ROGUS WWTW | HOLCOMBE ROGUS STW_SO_HOLCOMBE ROGUS | SWWA 2475 | SWWA 2475 | A2 | Inlet SO at WwTW | ST 0580 1824 | GB108045015020 | Spratford Stream | TRIB OF RIVER LYNER |  |  | Commissioned in 2019 - full year data expected | 241.06 | 93 | 100
South West Water | HOLCOMBE ROGUS WWTW | HOLCOMBE ROGUS STW_SSO_HOLCOMBE ROGUS | SWWA 2475 | SWWA 2475 | A3 | Storm tank at WwTW | ST 0639 1798 | GB108045015020 | Spratford Stream | TRIB OF RIVER LYNER |  |  | Commissioned in 2019 - full year data expected | 1221.22 | 126 | 95
South West Water | HOLLOWAY STREET CSO | HOLLOWAY ST_CSO_EXETER | 201925 | 201925 | A1 | SO on sewer network | SX 9223 9188 | GB108045009040 | Exe (Creedy to Estuary) | RIVER EXE VIA SWS | Exe |  | Commissioned in 2018 - full year data expected | 0 | 0 | 81 | Telemetry or data archiving failure / issue | Resolved - June
South West Water | HOLNE WWTW | HOLNE STW_SO_HOLNE | SWWA 2251 | SWWA 2251 | A2 | Inlet SO at WwTW | SX 7082 6856 | GB108046008350 | Dart | HOLY BROOK |  |  | Commissioned in 2019 - full year data expected | 1275.53 | 130 | 100
South West Water | HOLSWORTHY (VIADUCT) SO | HOLSWORTHY BRIDGE_CSO_HOLSWORTHY | 302143 | 302143/CS/01 | A1 | SO on sewer network | SS 3460 0350 | GB108047013880 | Deer | TRIB OF RIVER DEER (S) |  |  | EDM to be installed by December 2023
South West Water | HOMER PARK CSO | HOMER PARK_CSO_SALTASH | 302586 | 302586 | A1 | SO on sewer network | SX 4200 5958 | 71 | #N/A | TRIBUTARY OF SALTMILL CREEK(S) | Tamar |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | HOMERS LANE CSO | HOMERS LN_CSO_KINGSTEIGNTON | 201765 | 201765 | A1 | SO on sewer network | SX 8677 7285 | 22 | #N/A | TRIB O RIV.TEIGN VIA SW SEWER |  |  | Commissioned in 2017 - full year data expected | 1564.5 | 119 | 100
South West Water | HONICKNOWLE LANE CSO | HONICKNOWLE LANE_CSO_PLYMOUTH | 301712 | 301712 | A1 | SO on sewer network | SX 4704 5795 | 73 | #N/A | HAM BROOK |  | PLYMOUTH HOE (EAST) | Commissioned in 2017 - full year data expected | 173.04 | 82 | 100
South West Water | HONITON WASTEWATER TREATMENT WORKS | HONITON STW_SO_HONITON | NRA-SW-3869 | NRA-SW-3869 | A2 | Inlet SO at WwTW | ST 1522 0094 | GB108045009180 | Middle River Otter | RIVER OTTER |  |  | Commissioned in 2019 - full year data expected | 1050.15 | 130 | 100
South West Water | HONITON WASTEWATER TREATMENT WORKS | HONITON STW_SSO_HONITON | NRA-SW-3869 | NRA-SW-3869 | A3 | Storm tank at WwTW | ST 1522 0094 | GB108045009180 | Middle River Otter | RIVER OTTER |  |  | Commissioned in 2019 - full year data expected | 3709.13 | 192 | 100
South West Water | HOOE LAKE PUMPING STATION | HOOE LAKE SPST_PSCSOEO_PLYMSTOCK | 032894/PC/01 | 32894 | A1 | Storm discharge at pumping station | SX 4981 5261 | 73 | #N/A | HOOE LAKE, PLYM ESTUARY |  | PLYMOUTH HOE (EAST & WEST) | Commissioned pre-2016 - full year data expected | 7.5 | 5 | 54 | Installation set-up/design issue | Resolved - November
South West Water | HOOE ROAD CSO | HOOE ROAD_CSO_PLYMOUTH | 301811 | 301811 | A1 | SO on sewer network | SX 4981 5261 | 73 | #N/A | HOOE LAKE VIA SWS (ESTUARINE) |  | PLYMOUTH HOE (EAST) | Commissioned in 2017 - full year data expected | 8.7 | 22 | 100
South West Water | HORN BRIDGE PSEO/CSO | HORN BRIDGE SPST_PSCSOEO_LYME REGIS | 003956/PC/01 | 003956/PC/01 | A1 | Storm discharge at pumping station | SY 3366 9286 | GB108044009760 | Lim | RIVER LIM |  | LYME REGIS CHURCH CLIFF BEACH | Commissioned pre-2016 - full year data expected | 130.29 | 34 | 100
South West Water | HORNS CROSS SEWAGE TREATMENT WORKS | HORNS CROSS STW_SO_HORNS CROSS | 200403 | 200403/CS/01 | A2 | Inlet SO at WwTW | SS 3885 2320 | GB108050014470 | Upper River Yeo (Bideford) | TRIBUTARY OF RIVER YEO |  |  | EDM to be installed by December 2023
South West Water | HORNS CLOSE CSO | HORNS PARK_CSO_BISHOPSTEIGNTON | 203090 | 203090 | A1 | SO on sewer network | SX 9044 7360 | 22 | #N/A | SURFACE WATER SEWER (S) | Teign |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | HORRABRIDGE WWTW | HORRABRIDGE STW_SSO_HORRABRIDGE | 302126 | 302126 | A2 | Storm tank at WwTW | SX 4977 7043 | GB108047007870 | Walkham | RIVER WALKHAM |  |  | Commissioned in 2018 - full year data expected | 2134.1 | 126 | 100
South West Water | HORSLEARS PUMPING STATION | HORSLEARS SPST_PSCSOEO_AXMINSTER | 203701 | 203701 | A1 | Storm discharge at pumping station | SY 2881 9773 | GB108045008870 | Lower Axe | RIVER AXE(S) |  |  | Commissioned pre-2016 - full year data expected | 396.53 | 52 | 100
South West Water | HOWELL ROAD CSO | HOWELL ROAD_CSO_EXETER | 201376 | 201376 | A1 | SO on sewer network | SX 9146 9250 | GB108045009040 | Exe (Creedy to Estuary) | HIGHER LEAT VIA SWS | Exe |  | Commissioned in 2018 - full year data expected | 74.93 | 9 | 100
South West Water | ILSHAM MARINE DRIVE CSO | ILSHAM MARINE DRIVE_CSO_TORQUAY | 200227/CS/01 | 200227 | A1 | SO on sewer network | SX 9493 6358 | 409 | #N/A | TOR BAY (COASTAL) |  |  | Commissioned in 2017 - full year data expected | #N/A | #N/A | 0 | Installation set-up/design issue | N/A - Ongoing investigation
South West Water | ILSHAM ROAD CSO | ILSHAM RD_CSO_TORQUAY | 200228 | 200228 | A1 | SO on sewer network | SX 9375 6391 | 409 | #N/A | (S) ILSHAM VALLEY STREAM |  | MEADFOOT BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | ILSHAM VALLEY PUMPING STATION | ILSHAM VALLEY SPST_PSCSOEO_TORQUAY | 200977 | 200977 | A1 | Storm discharge at pumping station | SX 9494 6258 | 409 | #N/A | ENGLISH CHANNEL(C) |  | MEADFOOT BEACH | Commissioned pre-2016 - full year data expected | 1175.14 | 93 | 92
South West Water | IMPERIAL ROAD TANK CSO | IMPERIAL RD - TANK_CSO_EXMOUTH | 200123/CS/01 | 200123/CS/01 | A1 | SO on sewer network | SX 9986 8111 | 19 | #N/A | EXE ESTUARY | Exe | EXMOUTH BEACH | Commissioned pre-2016 - full year data expected | 102.4 | 15 | 100
South West Water | INDIAN QUEENS PSCSO/EO | INDIAN QUEENS SPS_PSCSOEO_INDIAN QUEENS | 301620 | 301620/PC/01 | A1 | Storm discharge at pumping station | SW 9372 5870 | GB108048001390 | Upper River Fal | RIVER FAL (S) |  |  | EDM to be installed by December 2023
South West Water | INNER HOPE PSCSO/EO | INNER HOPE COVE SPS_PSCSOEO_HOPE COVE | 202606 | 202606 | A1 | Storm discharge at pumping station | SX 6741 3976 | 266 | #N/A | HOPE COVE(C) |  | HOPE COVE BEACH | Commissioned pre-2016 - full year data expected | 1.61 | 5 | 100
South West Water | INSTOW A PUMPING STATION | INSTOW A SPS_PSCSOEO_INSTOW | 203125 | 203125 | A1 | Storm discharge at pumping station | SS 4719 3020 | 198 | #N/A | RIVER TORRIDGE ESTUARY (E) | Taw/Torridge | INSTOW BEACH | Commissioned pre-2016 - full year data expected | 40.7 | 11 | 100
South West Water | IPPLEPEN WASTEWATER TREATMENT WORKS | IPPLEPEN STW_SO_IPPLEPEN | 203406 | 203406 | A2 | Inlet SO at WwTW | SX 8281 6675 | GB108046005210 | Am Brook | HALWELL STREAM |  |  | Commissioned in 2019 - full year data expected | 167.77 | 59 | 93
South West Water | IPPLEPEN WASTEWATER TREATMENT WORKS | IPPLEPEN STW_SSO_IPPLEPEN | 203406 | 203406 | A3 | Storm tank at WwTW | SX 8281 6675 | GB108046005210 | Am Brook | HALWELL STREAM |  |  | Commissioned in 2019 - full year data expected | 509.96 | 34 | 100
South West Water | IVYBRIDGE STW | IVYBRIDGE STW_SSO_IVYBRIDGE | 203299 | 203299 | A2 | Storm tank at WwTW | SX 6316 5566 | GB108046005200 | Erme | RIVER ERME |  | MOTHECOMBE BEACH | Commissioned pre-2016 - full year data expected | 425.85 | 40 | 100
South West Water | IVYBRIDGE STW | IVYBRIDGE STW_SSO_IVYBRIDGE | 203299 | 203299 | A2 | Storm tank at WwTW | SX 6316 5566 | GB108046005200 | Erme | RIVER ERME |  | MOTHECOMBE BEACH | Commissioned pre-2016 - full year data expected | 1175.78 | 56 | 100
South West Water | BAMPTON STREET CSO | J/O BAMPTON ST/NEWPORT ST_CSO_TIVERTON | 201822 | 201822 | A1 | SO on sewer network | SS 9535 1280 | GB108045015050 | Exe (Barle to Culm) | RIVER EXE |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 100
South West Water | CHURCH ROAD CSO | J/O CHURCH RD/WESTWOOD_CSO_COCKWOOD | 202628 | 202628 | A1 | SO on sewer network | SX 9718 8063 | 20 | #N/A | COFTON STREAM(S) | Exe |  | Commissioned pre-2016 - full year data expected | 0.11 | 2 | 100
South West Water | COWLEYMOOR ESTATE CSO | J/O COWLEY MOOR/CHAPLE ST_CSO_TIVERTON | 201960 | 201960 | A1 | SO on sewer network | SS 9610 1299 | GB108045015030 | Lowman | TRIB OF RIVER LOWMAN VIA SWS |  |  | Commissioned in 2016 - full year data expected | 2.23 | 11 | 100
South West Water | BARRINGTON STREET CSO | J/O GOLD/BARRINGTON ST_CSO_TIVERTON | 201820/CS/01 | 201820 | A1 | SO on sewer network | SS 9577 1258 | GB108045015030 | Lowman | RIVER LOWMAN |  |  | Commissioned in 2018 - full year data expected | 1.49 | 9 | 100
South West Water | JACOBSTOW STW | JACOBSTOW STW_SO_JACOBSTOW | 302127 | 302127/CS/01 | A2 | Inlet SO at WwTW | SX 2024 9582 | GB108049007240 | Jacob Stream | TRIB OF RIVER NEED (S) |  |  | EDM to be installed by December 2023
South West Water | JERICHO CSO | JERICHO_CSO_LYME REGIS | 003955/CS/01 | 003955/CS/01 | A1 | SO on sewer network | SY 3402 9251 | GB108044009760 | Lim | RIVER LIM |  | LYME REGIS CHURCH CLIFF BEACH | Commissioned pre-2016 - full year data expected | 7.7 | 12 | 100
South West Water | JETTY PUMPING STATION | JETTY_PSCSOEO_PLYMOUTH | 301984 | 301984 | A1 | Storm discharge at pumping station | SX 4998 5401 | 73 | #N/A | RIVER PLYM ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 3.99 | 2 | 100
South West Water | JEWSONS YARD CSO | JEWSONS YARD M.H 27_CSO_CREDITON | 201866 | 201866/CS/01 | A1 | SO on sewer network | SX 8474 9920 | GB108045009280 | Lower Yeo (Creedy) | RIVER YEO (S) |  |  | EDM to be installed by December 2023
South West Water | JOCKEY HILL CSO | JOCKEY HILL_CSO_CREDITON | 201869 | 201869 | A1 | SO on sewer network | SS 8448 0041 | GB108045009090 | Middle Creedy | TRIBUTARY OF IVER CREEDY |  |  | Commissioned in 2018 - full year data expected | 4.83 | 22 | 94
South West Water | FRADDON JUNCTION CSO | JUNCTION A39 FRADDON_CSO_FRADDON | 301843 | 301843/CS/01 | A1 | SO on sewer network | SW 9126 5832 | GB108049000230 | Gannel (Upper) | RIVER GANNEL(S) |  |  | EDM to be installed by December 2023
South West Water | KENN AND KENNFORD PUMPING STATION | KENN/KENNFORD SPS_PSCSOEO_KENNFORD | 202371 | 202371 | A1 | Storm discharge at pumping station | SX 9275 8527 | GB108045009010 | Kenn | RIVER KENN |  |  | Commissioned in 2016 - full year data expected | 3657.2 | 186 | 100
South West Water | KEYBERRY ROAD NO.18 CSO | KEYBERRY RD ADJ NO 18_CSO_NEWTON ABBOT | 203200 | 203200 | A1 | SO on sewer network | SX 8703 7065 | GB108046005350 | Aller Brook (Teign) - Lower | ALLER BROOK(S) | Teign |  | Commissioned pre-2016 - full year data expected | 163.08 | 63 | 100
South West Water | KEYBERRY ROAD NO 2 | KEYBERRY RD NO 2_CSO_NEWTON ABBOT | 203199 | 203199 | A1 | SO on sewer network | SX 8703 7069 | GB108046005350 | Aller Brook (Teign) - Lower | THE ALLER BROOK (S) | Teign |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | O/S 4 KEYBERRY ROAD CSO | KEYBERRY RD NO 4_CSO_NEWTON ABBOT | 203100 | 203100 | A1 | SO on sewer network | SX 8703 7069 | GB108046005350 | Aller Brook (Teign) - Lower | SURFACE WATER SEWER(S) | Teign |  | Commissioned pre-2016 - full year data expected | 63.77 | 16 | 100
South West Water | BUCKFASTLEIGH STW | KILBURY STW_SO_BUCKFASTLEIGH | NRA-SW-5004 | NRA-SW-5004 | A2 | Inlet SO at WwTW | SX 7513 6581 | GB108046008350 | Dart | RIVER DART |  |  | Commissioned in 2019 - full year data expected | 773.8 | 112 | 100
South West Water | BUCKFASTLEIGH STW | KILBURY STW_SSO_BUCKFASTLEIGH | NRA-SW-5003 | NRA-SW-5003 | A3 | Storm tank at WwTW | SX 7513 6581 | GB108046008350 | Dart | RIVER DART |  |  | Commissioned in 2019 - full year data expected | 1340.15 | 107 | 100
South West Water | KILKHAMPTON WWTW | KILKHAMPTON STW_SSO_KILKHAMPTON | 15/49/30/P/10 | 15/49/30/P/10 | A2 | Storm tank at WwTW | SS 2504 1163 | GB108049013760 | Coombe Valley Stream | TRIB OF COOMBE VALLEY STREAM |  |  | Commissioned in 2019 - full year data expected | 1398.3 | 93 | 100
South West Water | CSO AT KILLIGREW STREET | KILLIGREW ST_CSO_FALMOUTH | 303015 | 303015 | A1 | SO on sewer network | SW 8083 3302 | 402 | #N/A | PENRYN RIVER(E) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | KILMINGTON WWTW | KILMINGTON STW_SSO_AXMINSTER | DRA 1559 | DRA 1559 | A2 | Storm tank at WwTW | SY 2786 9759 | GB108045008870 | Lower Axe | RIVER AXE |  |  | Commissioned in 2019 - full year data expected | 1482.3 | 186 | 100
South West Water | KILN QUAY PUMPING STATION | KILN QUAY SPS_PSCSOEO_NEWTON FERRERS | 301629 | 301629 | A1 | Storm discharge at pumping station | SX 5445 4785 | 70 | #N/A | NEWTON CREEK (ESTUARINE) | Yealm |  | Commissioned in 2017 - full year data expected | 1.5 | 3 | 100
South West Water | GALMPTON PUMPING STATION | KILN ROAD SPS_PSCSOEO_GALMPTON | 202732 | 202732 | A1 | Storm discharge at pumping station | SX 8831 5621 | 23 | #N/A | GALMPTON STREAM | Dart |  | Commissioned pre-2016 - full year data expected | 2.34 | 7 | 100
South West Water | KING STREET CSO | KING ST_CSO_TRURO | 301801 | 301801 | A1 | SO on sewer network | SW 8257 4476 | GB108048002340 | Kenwyn | RIVER KENWYN VIA SWS | Fal Estuary |  | Commissioned in 2018 - full year data expected | 1.1 | 6 | 79 | Sensor failure / issue | Resolved - December
South West Water | KINGS BRIDGE CSO | KINGS BRIDGE_CSO_MORETONHAMPSTEAD | 201691 | 201691/CS/01 | A1 | SO on sewer network | SX 7600 8571 | GB108046008330 | Wray Brook | WRAY BROOK (S) |  |  | EDM to be installed by December 2023
South West Water | KINGS DRIVE CSO | KINGS DRIVE PENSTOCK_CSO_TORQUAY | 200229 | 200229 | A1 | SO on sewer network | SX 9068 6371 | 429 | #N/A | KINGS DRIVE STREAM TO SEA |  | TORRE ABBEY BEACH | Commissioned pre-2016 - full year data expected | 1.58 | 2 | 100
South West Water | KINGS NYMPTON NORTH STW | KINGS NYMPTON NORTH STW_SO_KINGS NYMPTON | 204041 | 204041 | A2 | Inlet SO at WwTW | SS 6787 1950 | GB108050014380 | Mole (Taw to Bray) | TRIBUTARY OF RIVER MOLE |  |  | EDM to be installed by December 2023
South West Water | KINGSCOTT STW | KINGSCOTT STW_SO_KINGSCOTT | 200928 | 200928/CS/02 | A2 | Inlet SO at WwTW | SS 5422 1785 | GB108050014350 | Whitsleigh Down Brook | (S) DODSCOTT BROOK |  |  | EDM to be installed by December 2023
South West Water | KINGSTON WWTW | KINGSTON STW_SSO_KINGSTON | 203413 | 203413 | A2 | Storm tank at WwTW | SX 6385 4739 | 266 | #N/A | KINGSTON STREAM |  |  | Commissioned in 2019 - full year data expected | 1868.34 | 114 | 100
South West Water | KINGSWOOD ROAD PUMPING STATION | KINGSWOOD ROAD SPS_PSCSOEO_GUNNISLAKE | 301617 | 301617 | A1 | Storm discharge at pumping station | SX 4357 7151 | GB108047007860 | Lower River Tamar | RIVER TAMAR |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 100
South West Water | KINTERBURY CREEK PUMPING STATION | KINTERBURY CREEK_PSCSOEO_PLYMOUTH | 301593 | 301593 | A1 | Storm discharge at pumping station | SX 4356 5815 | 73 | #N/A | RIVER TAMAR VIASWS (ESTUARINE) |  |  | Commissioned in 2016 - full year data expected | 154.86 | 16 | 100
South West Water | KNAVE-GO-BYE COMBINED SEWER OVERFLO | KNAVE-GO-BY_CSO_CAMBORNE | 300701 | 300701 | A1 | SO on sewer network | SW 6523 3899 | GB108049000600 | Red River (Upper) | TRIB OF ROSEWORTHY STREAM |  |  | Commissioned in 2019 - full year data expected | 841.22 | 69 | 85 | Sensor failure / issue | Resolved - June
South West Water | KNOWLE WASTEWATER TREATMENT WORKS | KNOWLE STW_SO_BRAUNTON | 202367 | 202367 | A2 | Inlet SO at WwTW | SS 4919 3839 | GB108050020010 | Lower Caen | TRIBUTARY OF RIVER CAEN |  |  | Commissioned in 2017 - full year data expected | 686.27 | 76 | 99
South West Water | EAST KNOWSTONE STW | KNOWSTONE EAST STW_SO_KNOWSTONE | SWWA 108 | SWWA 108 | A2 | Inlet SO at WwTW | SS 8370 2310 | GB108050014120 | Crooked Oak | TRIBUTARY OF CROOKED OAK |  |  | EDM to be installed by December 2023
South West Water | LADOCK VALLEY STW | LADOCK VALLEY STW_SSO_TRESILLIAN | 302508 | 302508 | A2 | Storm tank at WwTW | SW 8709 4704 | GB108048002350 | Tresillian River (Lower) | TRESILLIAN RIVER ESTUARY(E) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 789.45 | 74 | 100
South West Water | LAFLOUDER LANE PUMPING STATION | LAFLOUDER LANE SPS_PSCSOEO_MULLION | 302948 | 302948 | A1 | Storm discharge at pumping station | SW 6651 1902 | 269 | #N/A | ENGLISH CHANNEL (COASTAL) |  |  | Commissioned in 2018 - full year data expected | 6.77 | 5 | 100
South West Water | LAIRA AVENUE CSO | LAIRA AV_CSO_PLYMOUTH | 301784 | 301784 | A1 | SO on sewer network | SX 5078 5584 | 73 | #N/A | RIVER PLYM VIA SWS (ESTUARINE) |  |  | Commissioned in 2016 - full year data expected | 0.83 | 1 | 100
South West Water | LAKE LANE PUMPING STATION | LAKE LANE_PSCSOEO_LISKEARD | 301852 | 301852 | A1 | Storm discharge at pumping station | SX 2621 6447 | GB108048002320 | Seaton | TRIB OF RIVER SEATON |  |  | Commissioned in 2020 - full year data expected | 22.42 | 4 | 100
South West Water | LAKE LANE CSO | LAKE LN_CSO_DOUSLAND | 301840 | 301840/CS/01 | A1 | SO on sewer network | SX 5313 6804 | GB108047003660 | Meavy | RIVER MEAVY (S) |  |  | EDM to be installed by December 2023
South West Water | LANDKEY PUMPING STATION | LANDKEY SPS_PSCSOEO_LANDKEY | 200195/PC/01 | 200195 | A1 | Storm discharge at pumping station | SS 5909 3103 | GB108050014620 | Venn | RIVER VENN | Taw/Torridge |  | Commissioned in 2016 - full year data expected | 283.2 | 49 | 100
South West Water | LANDRAKE PUMPING STATION | LANDRAKE SPS_PSCSOEO_LANDRAKE | 301621 | 301621 | A1 | Storm discharge at pumping station | SX 3783 6073 | 72 | #N/A | TRIBUTARY OF THE RIVER LYNER |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 100
South West Water | LANDRAKE WASTEWATER TREATMENT WORKS | LANDRAKE STW_SO_LANDRAKE | 303086 | 303086 | A2 | Inlet SO at WwTW | SX 3795 6095 | 72 | #N/A | LANDRAKE STREAM |  |  | Commissioned in 2019 - full year data expected | 204.21 | 79 | 100
South West Water | LANGATON LANE CSO | LANGATON LN_CSO_EXETER | 201852 | 201852 | A1 | SO on sewer network | SX 9731 9413 | GB108045008860 | Upper Clyst | PIN BROOK | Exe |  | Commissioned in 2018 - full year data expected | 26.29 | 21 | 97
South West Water | LANGORE PUMPING STATION | LANGORE SPS_PSCSOEO_LAUNCESTON | 301581 | 301581 | A1 | Storm discharge at pumping station | SX 2966 8658 | GB108047007981 | Lower River Ottery | TRIBUTARY OF THE RIVER OTTER |  |  | Commissioned in 2020 - full year data expected | 30.02 | 22 | 100
South West Water | LANGTREE STW SEPTIC TANK | LANGTREE STW_SO_LANGTREE | 202198/CS/01 | 202198/CS/01 | A2 | Inlet SO at WwTW | SS 4497 1535 | GB108050014330 | Langtree Lake | TRIBUTARY OF RIVER TORRIDGE(S) |  |  | EDM to be installed by December 2023
South West Water | LANHYDROCK ROAD CSO | LANHYDROCK ROAD_CSO_PLYMOUTH | 301788 | 301788/CS/01 | A1 | SO on sewer network | SX 5016 5478 | 73 | #N/A | RIVER PLYM (E) |  |  | Commissioned in 2016 - full year data expected | 14.93 | 19 | 100
South West Water | LANREATH PUMPING STATION | LANREATH SPS_PSCSOEO_LANREATH | NRA-SW-3210 | NRA-SW-3210 | A1 | Storm discharge at pumping station | SX 1808 5677 | GB108048001340 | Pont Pill | TRIBUTARY OF PONT PILL |  |  | Commissioned in 2018 - full year data expected | 325.23 | 65 | 100
South West Water | LARKBEARE HOUSE CSO | LARKBEARE HSE_CSO_EXETER | 201928 | 201928 | A1 | SO on sewer network | SX 9223 9189 | GB108045009040 | Exe (Creedy to Estuary) | RIVER EXE VIA SWS | Exe |  | Commissioned in 2018 - full year data expected | 0 | 0 | 65 | Sensor failure / issue | Resolved - December
South West Water | LAUREL AVENUE CSO | LAUREL AVE_CSO_BIDEFORD | 201945 | 201945 | A1 | SO on sewer network | SS 4385 2605 | GB108050014500 | Kenwith Stream | KENWITH STREAM | Taw/Torridge |  | Commissioned in 2018 - full year data expected | 1.9 | 6 | 100
South West Water | LAUREL LANE CSO | LAUREL LN_CSO_SHALDON | 203084 | 203084 | A1 | SO on sewer network | SX 9258 7214 | 22 | #N/A | RINGMORE STREAM (S) | Teign |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | LEE MILL PUMPING STATION | LEE MILL SPS_PSCSOEO_PLYMOUTH | 301626 | 301626 | A1 | Storm discharge at pumping station | SX 5994 5568 | GB108047004010 | Lower River Yealm | RIVER YEALM |  |  | Commissioned pre-2016 - full year data expected | 210.17 | 31 | 100
South West Water | MYLOR BRIDGE PSCSO/EO | LEMON ARMS SPST_PSCSOEO_MYLOR BRIDGE | 301654 | 301654/PC/02 | A1 | Storm discharge at pumping station | SW 8052 3604 | 76 | #N/A | MYLOR CREEK (E) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 113.77 | 14 | 100
South West Water | LEMON MEWS CSO | LEMON MEWS_CSO_TRURO | 302682 | 302682 | A1 | SO on sewer network | SW 8256 4474 | GB108048002340 | Kenwyn | RIVER KENWYN(S) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | NO 15 LEMON ROAD CSO | LEMON RD_CSO_NEWTON ABBOT | 203138 | 203138 | A1 | SO on sewer network | SX 8636 7144 | 22 | #N/A | RIVER LEMON (S) | Teign |  | Commissioned pre-2016 - full year data expected | 662.37 | 210 | 100 |  |  | Data collection - Tidal / river inundation | N/A - Ongoing investigation | SOAF N/A - Proposed SFTP (overflow previously improved)
South West Water | LEONARDS COVE PS | LEONARDS COVE_PSCSOEO_STOKE FLEMING | 203368 | 203368 | A1 | Storm discharge at pumping station | SX 8661 4824 | 260 | #N/A | LEONARDS COVE STREAM (S) | Dart |  | Jan 2021 | 0 | 0 | 100
South West Water | LERRYN CAR PARK OVERFLOW | LERRYN CAR PARK SPS_PSCSOEO_LOSTWITHIEL | 2895/92 | 2895/92 | A1 | Storm discharge at pumping station | SX 1401 5707 | 26 | #N/A | TIDAL RIVER LERRYN |  |  | Commissioned in 2018 - full year data expected | 404.97 | 58 | 100
South West Water | LEUSDON STW | LEUSDON STW_SO_LEUSDON | SWWA 422 | SWWA 422 | A2 | Inlet SO at WwTW | SX 7126 7279 | GB108046005250 | Webburn | TRIBUTARY OF RIVER WEBBURN |  |  | EDM to be installed by December 2023
South West Water | LEWDOWN WASTEWATER TREATMENT WORKS | LEWDOWN STW_SO_LEWDOWN | NRA-SW-6982 | NRA-SW-6982 | A2 | Inlet SO at WwTW | SX 4478 8691 | GB108047008010 | Thrushel | TRIBUTARY OF RIVER THRUSHEL |  |  | Commissioned in 2018 - full year data expected | 462.76 | 78 | 100
South West Water | LEWDOWN WASTEWATER TREATMENT WORKS | LEWDOWN STW_SSO_LEWDOWN | NRA-SW-6982 | NRA-SW-6982 | A3 | Storm tank at WwTW | SX 4478 8691 | GB108047008010 | Thrushel | TRIBUTARY OF RIVER THRUSHEL |  |  | Commissioned in 2018 - full year data expected | 880.81 | 65 | 100
South West Water | LEZANT PSCSO/EO | LEZANT SPS_PSCSOEO_LEZANT | 301627 | 301627/PC/01 | A1 | Storm discharge at pumping station | SX 3386 7920 | GB108047007920 | Lowley Brook | RIVER INNY (S) |  |  | EDM to be installed by December 2023
South West Water | LIFTON WASTEWATER TREATMENT WORKS | LIFTON STW_SO_LIFTON | 15/47/52/P/11 | 15/47/52/P/11 | A2 | Inlet SO at WwTW | SX 3925 8506 | GB108047008010 | Thrushel | RIVER THRUSHEL |  |  | Commissioned in 2018 - full year data expected | 494.82 | 97 | 100
South West Water | LIME KILN TANK CSO | LIME KILN PS_CSO_BUDLEIGH SALTERTON | 200111/CS/01 | 200111/CS/01 | A1 | SO on sewer network | SY 0794 8192 | 408 | #N/A | ENGLISH CHANNEL |  | BUDLEIGH SALTERTON BEACH | Commissioned pre-2016 - full year data expected | 432.95 | 48 | 100
South West Water | MARDON SSO | LIME ST_CSO_MORETONHAMPSTEAD | NRA-SW-5473 | NRA-SW-5473 | A1 | SO on sewer network | SX 7553 8628 | GB108046008330 | Wray Brook | THE WRAY BROOK |  |  | EDM to be installed by December 2023
South West Water | LIPSON VALE 1 CSO | LIPSON VALE 1_CSO_PLYMOUTH | 301774 | 301774 | A1 | SO on sewer network | SX 4935 5564 | 73 | #N/A | TRIB OF THE RIVER PLYM VIA SWS |  | PLYMOUTH HOE (WEST) | Commissioned in 2020 - full year data expected | 120.03 | 91 | 100
South West Water | LITTLE KNOWLE CSO | LITTLE KNOWLE_CSO_BUDLEIGH SALTERTON | 200116/CS/01 | 200116/CS/01 | A1 | SO on sewer network | SY 0535 8226 | 408 | #N/A | KNOWLE STREAM |  | BUDLEIGH SALTERTON BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 59 | Sensor failure / issue | Resolved - September
South West Water | LITTLE PETHERICK WWTW | LITTLE PETHERICK STW_SO_WADEBRIDGE | NRA-SW-3676 | NRA-SW-3676 | A2 | Inlet SO at WwTW | SW 9182 7258 | 135 | #N/A | TRIB OF LITTLE PETHERICK CREEK | Camel |  | Commissioned pre-2016 - full year data expected | 497.65 | 83 | 100
South West Water | LITTLE SILVER PUMPING STATION | LITTLE SILVER SPST_PSCSOEO_TIVERTON | 203078 | 203078 | A1 | Storm discharge at pumping station | SS 9544 1208 | GB108045015030 | Lowman | RIVER LOWMAN |  |  | Commissioned pre-2016 - full year data expected | 998.33 | 99 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: Cost beneficial outcome not yet determined
South West Water | LITTLEGATE ROAD CSO | LITTLEGATE ROAD_CSO_PAIGNTON | 201011 | 201011 | A1 | SO on sewer network | SX 8984 6036 | 429 | #N/A | ENGLISH CHANNEL & VICT PARK WC |  | PAIGNTON (PAIGNTON SANDS) | Commissioned pre-2016 - full year data expected | 0.77 | 5 | 96
South West Water | LITTLEHAM STW | LITTLEHAM STW_SSO_LITTLEHAM | 203010 | 203010 | A2 | Storm tank at WwTW | SS 4353 2310 | GB108050014470 | Upper River Yeo (Bideford) | TRIB OF RIVER YEO(S) |  |  | EDM to be installed by December 2023
South West Water | LODDISWELL WWTW | LODDISWELL STW_SO_LODDISWELL | DRA 1349 | DRA 1349 | A2 | Inlet SO at WwTW | SX 7228 4800 | GB108046004900 | Avon - Lower | RIVER AVON | Avon |  | Commissioned in 2017 - full year data expected | 72.2 | 60 | 100
South West Water | LISKEARD STW | LODGEHILL STW_SSO_LISKEARD | NRA-SW-3789 | NRA-SW-3789 | A2 | Storm tank at WwTW | SX 2416 6306 | GB108048001440 | East Looe River | EAST LOOE RIVER |  | EAST LOOE BEACH | Commissioned pre-2016 - full year data expected | 986.04 | 90 | 100
South West Water | LONGROCK INDUSTRIAL ESTATE | LONGROCK IND ESTATE SPS_PSCSOEO_LONGROCK | 300272 | 300272/PC/01 | A1 | Storm discharge at pumping station | SW 4980 3112 | 405 | #N/A | MOUNTS BAY (C) |  | LONG ROCK | Commissioned pre-2016 - full year data expected | 0.57 | 2 | 100
South West Water | LORDS MEADOW WWTW | LORDS MEADOW STW_SO_CREDITON | NRA-SW-0215 | NRA-SW-0215 | A2 | Inlet SO at WwTW | SS 8488 0062 | GB108045009090 | Middle Creedy | RIVER YEO/RIVER CREEDY |  |  | Commissioned in 2018 - full year data expected | 21.07 | 34 | 88 | Comms failure / issue | Resolved - March
South West Water | LORDS MEADOW WWTW | LORDS MEADOW STW_SSO_CREDITON | NRA-SW-0215 | NRA-SW-0215 | A3 | Storm tank at WwTW | SS 8488 0062 | GB108045009090 | Middle Creedy | RIVER YEO/RIVER CREEDY |  |  | Commissioned in 2018 - full year data expected | 410.08 | 32 | 100
South West Water | LORNA IRWIN WALK | LORNA IRWIN SPST_PSCSOEO_COMBE MARTIN | 2674 | 2674 | A1 | Storm discharge at pumping station | SS 5788 4702 | GB108051020440 | Umber | RIVER UMBER (S) |  | COMBE MARTIN BEACH | Commissioned pre-2016 - full year data expected | 777.03 | 51 | 100
South West Water | LOVE LANE COMBINED SEWER OVERFLOW | LOVE LN_CSO_MARLDON | 201758 | 201758 | A1 | SO on sewer network | SX 8676 6361 | GB108046005340 | Aller Brook | TRIB OF ALLER BROOK | Teign |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | LOWER BOSCASWELL CSO | LOWER BOSCASWELL_CSO_ST JUST | 303094 | 303094 | A1 | SO on sewer network | SW 3717 3490 | GB610807680001 | Lands End to Trevose Head | ATANTIC OCEAN(C) |  |  | EDM to be installed by December 2023
South West Water | NORTHERN PUMPING STATION | LOWER CLOVELLY NORTHERN SPST_PSCSOEO_CLO | 203575 | 203575 | A1 | Storm discharge at pumping station | SS 3185 2493 | 236 | #N/A | CLOVELLY BAY (COASTAL WATERS) |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | SOUTHERN PUMPING STATION | LOWER CLOVELLY SOUTHERN SPST_PSCSOEO_CLO | 203576 | 203576 | A1 | Storm discharge at pumping station | SS 3202 2470 | 236 | #N/A | CLOVELLY BAY (COASTAL WATERS) |  |  | Commissioned in 2016 - full year data expected | 766.44 | 59 | 100
South West Water | LOWER COLLAPARK CSO | LOWER COLLAPARK_CSO_TOTNES | EPRDB3993NS | EPR/DB3993NS | A1 | SO on sewer network | SX 8005 6071 | 23 | #N/A | MALT MILL LAKE VIA SWS | Dart |  | Commissioned in 2018 - full year data expected | 2.73 | 3 | 100
South West Water | LOWER FERRY PUMPING STATION | LOWER FERRY SPS_PSCSOEO_KINGSWEAR | 200160/PC/01 | 200160 | A1 | Storm discharge at pumping station | SX 8812 5103 | 23 | #N/A | RIVER DART (ESTUARINE) |  |  | Commissioned in 2017 - full year data expected | 126.27 | 71 | 100
South West Water | LOWER PARK ROAD PUMPING STATION | LOWER PARK ROAD SPS_PSCSOEO_BRAUNTON | 200211 | 200211 | A1 | Storm discharge at pumping station | SS 4935 3574 | GB108050020020 | Knowl Water | KNOWL WATER |  |  | Commissioned in 2018 - full year data expected | 21.71 | 12 | 100
South West Water | LOWER STICKER PUMPING STATION | LOWER STICKER SPS_PSCSOEO_ST AUSTELL | 301610 | 301610 | A1 | Storm discharge at pumping station | SW 9782 4973 | GB108048002250 | Caerhays Stream | CAERHAYS STREAM |  |  | Commissioned in 2019 - full year data expected | 10.15 | 6 | 100
South West Water | LOWICKE HOUSE PS | LOWICKE HSE SPS_PSCSOEO_NEWTON ABBOT | 203102 | 203102 | A1 | Storm discharge at pumping station | SX 8492 7228 | 22 | #N/A | THE ALLER BROOK (S) | Teign |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | LUCKETT WASTEWATER TREATMENT WORKS | LUCKETT STW_SO_CALLINGTON | 33938 | 33938 | A2 | Inlet SO at WwTW | SX 3907 7366 | GB108047007860 | Lower River Tamar | ALREN STREAM |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 95
South West Water | LUDGVAN SCHOOL CSO | LUDGVAN SCHOOL_CSO_CROWLAS | 302301/CS/01 | 302301 | A1 | SO on sewer network | SW 5132 3307 | GB108048002110 | Marazion River | LUDGVAN STREAM |  |  | Commissioned in 2018 - full year data expected | 136.52 | 24 | 100
South West Water | LUSTLEIGH WASTEWATER TREATMENT WORK | LUSTLEIGH STW_SSO_BOVEY TRACEY | NRA-SW-7351 | NRA-SW-7351 | A2 | Storm tank at WwTW | SX 7868 8093 | GB108046008330 | Wray Brook | WRAY BROOK | Teign |  | Commissioned in 2017 - full year data expected | 1184.16 | 80 | 100
South West Water | ST AUSTELL NORTH STW | LUXULYAN STW_SSO_ST AUSTELL | SWWA 146 | SWWA 146 | A2 | Storm tank at WwTW | SX 0432 5820 | GB108048002310 | Par River (Upper) | (S) RIVER PAR |  | PAR SANDS | Commissioned pre-2016 - full year data expected | 653.78 | 55 | 100
South West Water | LOWER MILL COMBINED SEWER OVERFLOW | LWR MILL_CSO_DULVERTON | 202233 | 202233 | A1 | SO on sewer network | SS 9125 2772 | GB108045015100 | Lower Barle | RIVER BARLE |  |  | Commissioned in 2019 - full year data expected | 3.45 | 14 | 94
South West Water | LOWER NORTH STREET CSO | LWR NORTH ST I_CSO_EXETER | 201373 | 201373 | A1 | SO on sewer network | SX 9147 9250 | GB108045009040 | Exe (Creedy to Estuary) | HIGHER LEAT VIA SW SEWER | Exe |  | Commissioned in 2016 - full year data expected | 213.82 | 71 | 98.9
South West Water | LYMPSTONE OUTFALL PUMPING STATION | LYMPSTONE OUTFALL SPS_PSCSO_LYMPSTONE | 202165 | 202165 | A1 | SO on sewer network | SX 9874 8386 | 19 | #N/A | RIVER EXE ESTUARY | Exe |  | Commissioned pre-2016 - full year data expected | 14.23 | 13 | 100
South West Water | LYNMOUTH (MANOR GARDENS) STW | LYNMOUTH STW_SSO_LYNMOUTH | 202404 | 202404 | A2 | Storm tank at WwTW | SS 7238 5023 | 237 | #N/A | LYNMOUTH BAY(C) |  | LYNMOUTH BEACH | Commissioned pre-2016 - full year data expected | 33.61 | 5 | 100
South West Water | MACEY STEPS CSO | MACEY STEPS_CSO_TORPOINT | 301888 | 301888 | A1 | SO on sewer network | SX 4399 5527 | 72 | #N/A | HAMOAZE (ESTUARINE) | Lynher |  | Commissioned in 2018 - full year data expected | 86.93 | 66 | 100
South West Water | MADEIRA DRIVE PSCSO/EO | MADEIRA DRIVE SPS_PSCSOEO_BUDE | 301648 | 301648/PC/01 | A1 | Storm discharge at pumping station | SS 2008 0252 | 234 | #N/A | WIDEMOUTH BAY (C) |  | WIDEMOUTH SAND | Commissioned pre-2016 - full year data expected | 305.51 | 50 | 100
South West Water | EXMOUTH SEWAGE TREATMENT WORKS | MAER LANE STW_SSO_EXMOUTH | 201965 | 201965 | A2 | Storm tank at WwTW | SY 0379 7919 | 408 | #N/A | LYME BAY(C) | Exe | SANDY BAY BEACH | Commissioned pre-2016 - full year data expected | 628.34 | 49 | 100
South West Water | MAER ROAD CSO EXMOUTH | MAER RD SPS_CSO_EXMOUTH | 200125/CS/01 | 200125/CS/01 | A1 | SO on sewer network | SY 0107 8006 | 19 | #N/A | LITTLEHAM BROOK | Exe | EXMOUTH BEACH | Commissioned pre-2016 - full year data expected | 1128.35 | 74 | 100
South West Water | MAER PUMPING STATION & TANK CSO | MAER ROAD SPST_PSCSOEO_EXMOUTH | 200126/PC/01 | 200126/PC/01 | A1 | Storm discharge at pumping station | SY 0111 7968 | 19 | #N/A | ENGLISH CHANNEL | Exe | EXMOUTH BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | MAGDALEN ROAD CSO | MAGDALEN RD_CSO_EXETER | 201923 | 201923 | A1 | SO on sewer network | SX 9223 9188 | GB108045009040 | Exe (Creedy to Estuary) | RIVER EXE VIA SWS | Exe |  | Commissioned in 2018 - full year data expected | 14.6 | 15 | 31 | Sensor failure / issue | Resolved - September
South West Water | MAIN ROAD CSO | MAIN RD_CSO_EXMINSTER | 201779 | 201779 | A1 | SO on sewer network | SX 9456 8732 | 20 | #N/A | BERRY BROOK | Exe |  | Commissioned in 2018 - full year data expected | 4.42 | 12 | 100
South West Water | THE OLD ORCHARD CSO | MAIN ST/TOWN ORCHARD_CSO_ABBOTSKERSWELL | 201814 | 201814 | A1 | SO on sewer network | SX 8566 6878 | GB108046005340 | Aller Brook | TRIB OF ALLER BROOK | Teign |  | Commissioned in 2017 - full year data expected | 214.3 | 86 | 96
South West Water | MALBOROUGH VILLAGE PUMPING STATION | MALBOROUGH STW_SO_SALCOMBE | 001685/PC/01 | 001685/PC/01 | A2 | Inlet SO at WwTW | SX 7118 3882 | 430 | #N/A | COMBE STREAM (S) |  | SALCOMBE SOUTH SANDS | Commissioned pre-2016 - full year data expected | 9.87 | 4 | 100
South West Water | MANOR HILL COMBINED SEWER OVERFLOW | MANOR HALL_CSO_HATHERLEIGH | 201771 | 201771 | A1 | SO on sewer network | SS 5402 0427 | GB108050008220 | Lower River Lew (Torridge) | RIVER LEW |  |  | Commissioned in 2019 - full year data expected | 152.2 | 61 | 67 | Sensor failure / issue | Resolved - January | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: Cost beneficial outcome not yet determined
South West Water | MANSTONE LANE CSO | MANSTONE LN_CSO_SIDMOUTH | 201835 | 201835 | A1 | SO on sewer network | SY 1262 8895 | GB108045009160 | Sid | WOOLBROOK |  |  | Commissioned in 2019 - full year data expected | 17.6 | 37 | 95
South West Water | BARN ORCHARD COTTAGES PS | MARHAMCHURCH SPS_PSCSOEO_BUDE | 302092 | 302092 | A1 | Storm discharge at pumping station | SS 2182 0376 | GB108049013730 | Upper River Strat | RIVER STRAT |  | SUMMERLEAZE | Commissioned in 2016 - full year data expected | 367.46 | 90 | 100
South West Water | MARINE PARADE CSO | MARINE PARADE_CSO_BUDLEIGH SALTERTON | 200114/CS/01 | 200114/CS/01 | A1 | SO on sewer network | SY 0664 8186 | 408 | #N/A | KNOWLE STREAM |  | BUDLEIGH SALTERTON BEACH | Commissioned pre-2016 - full year data expected | 31.18 | 11 | 66 | Comms failure / issue | Resolved - July
South West Water | MARINE ROAD NO 1 PUMPING STATION | MARINE ROAD NO1 SPS_PSCSOEO_PLYMSTOCK | 032893/PC/01 | 32893 | A1 | Storm discharge at pumping station | SX 4991 5332 | 73 | #N/A | THE CATTEWATER PLYM ESTUARY |  | PLYMOUTH HOE (EAST & WEST) | Commissioned pre-2016 - full year data expected | 3.08 | 3 | 100
South West Water | METHODIST CHURCH CSO | MARKET PLACE_CSO_CAMELFORD | 301836 | 301836/CS/01 | A1 | SO on sewer network | SX 1063 8373 | GB108049007060 | Upper River Camel | RIVER CAMEL (S) |  |  | EDM to be installed by December 2023
South West Water | LYNTON/LYNMOUTH SEWERAGE | MARKET PLACE_CSO_LYNTON | 004516/CS/01 | 004516/CS/01 | A1 | SO on sewer network | SS 7199 4936 | GB108051020600 | West Lyn River | LADY WELL STREAM (S) |  | LYNMOUTH BEACH | Commissioned pre-2016 - full year data expected | 186.72 | 35 | 87 | Sensor failure / issue | Resolved - March
South West Water | MARKET ROAD CSO | MARKET ROAD_CSO_PLYMPTON | 302253 | 302253 | A1 | SO on sewer network | SX 5361 5615 | 73 | #N/A | LONGBROOK |  | PLYMOUTH HOE (EAST) | Commissioned in 2016 - full year data expected | 173.93 | 49 | 100
South West Water | MARKET SQUARE CSO | MARKET SQUARE_CSO_CAMELFORD | 301835 | 301835/CS/01 | A1 | SO on sewer network | SX 1063 8373 | GB108049007060 | Upper River Camel | RIVER CAMEL (S) |  |  | EDM to be installed by December 2023
South West Water | CSO AT MARKET STREET | MARKET ST_CSO_FALMOUTH | 303017 | 303017 | A1 | SO on sewer network | SW 8083 3302 | 402 | #N/A | PENRYN RIVER | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | KINGSAND SEWAGE PUMPING STATION | MARKET STREET SPS_PSCSOEO_KINGSAND | 301903 | 301903/PC/01 | A1 | Storm discharge at pumping station | SX 4351 5044 | 400 | #N/A | CAWSAND BAY (C) |  | KINGSAND BEACH | Commissioned pre-2016 - full year data expected | 33.72 | 21 | 100
South West Water | KINGSAND SEWAGE PUMPING STATION | MARKET STREET SPS_PSCSOEO_KINGSAND | 301903 | 301903/PC/01 | A1 | Storm discharge at pumping station | SX 4348 5048 | 400 | #N/A | CAWSAND BAY (C) |  | KINGSAND BEACH | Commissioned pre-2016 - full year data expected | 33.72 | 21 | 100
South West Water | MARKET WALK CSO | MARKET WALK_CSO_NEWTON ABBOT | 203339 | 203339 | A1 | SO on sewer network | SX 8603 7139 | GB108046008450 | Lemon | RIVER LEMON(S) | Teign |  | Commissioned pre-2016 - full year data expected | 1.57 | 5 | 100
South West Water | MARSH MILLS PUMPING STATION | MARSH MILLS SPST_PSCSOEO_PLYMPTON | 302110 | 302110 | A1 | Storm discharge at pumping station | SX 5159 5619 | 73 | #N/A | RIVER PLYM (ESTUARINE) |  | PLYMOUTH HOE (EAST & WEST) | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | MARSH MILLS WWTW | MARSH MILLS STW_SSO_PLYMPTON | NRA-SW-6977 | NRA-SW-6977 | A2 | Storm tank at WwTW | SX 5201 5628 | 73 | #N/A | RIVER PLYM (ESTUARINE) |  | PLYMOUTH HOE (EAST) | Commissioned pre-2016 - full year data expected | 694.39 | 74 | 100
South West Water | MARY TAVY WWTW | MARY TAVY STW_SSO_MARY TAVY | 15/47/41/P/5 | 15/47/41/P/5 | A2 | Storm tank at WwTW | SX 5088 7831 | GB108047007950 | Upper River Tavy | CHOLWELL BROOK |  |  | Commissioned in 2018 - full year data expected | 2417.71 | 133 | 100 |  |  | Performance - Infiltration | Scheduled | Stage 1b: Confirmed "asset maintenance" issue
South West Water | MAUNSELL CLOSE CSO | MAUNSELL CLOSE_CSO_PLYMOUTH | 302615 | 302615 | A1 | SO on sewer network | SX 4561 5719 | 73 | #N/A | WESTON MILL LAKE VIA W'COURSE | Tamar |  | Commissioned pre-2016 - full year data expected | 0.56 | 2 | 100
South West Water | MAYORS AVENUE PUMPING STATION | MAYORS AVENUE_PSCSOEO_DARTMOUTH | 202401 | 202401 | A1 | Storm discharge at pumping station | SX 8801 5152 | 23 | #N/A | DART RIVER ESTUARY(E) |  | DARTMOUTH CASTLE AND SUGARY COVE | Commissioned pre-2016 - full year data expected | 73.37 | 65 | 90
South West Water | MEADOW ROAD TANK CSO | MEADOW RD SSO_CSO_BUDLEIGH SALTERTON | 200112/CS/01 | 200112/CS/01 | A1 | SO on sewer network | SY 0597 8206 | 408 | #N/A | KNOWLE STREAM |  | BUDLEIGH SALTERTON BEACH | Commissioned pre-2016 - full year data expected | 15.39 | 14 | 100
South West Water | CHILLINGTON COMBINED SEWER OVERFLOW | MEADOWSIDE CHILLINGTON_CSO | 203108 | 203108 | A1 | SO on sewer network | SX 7897 4266 | GB108046004760 | Avon (DevonTidal) and Sth Hams - Frogmore | TRIBUTARY OF FROGMORE CREEK | Salcombe |  | Commissioned in 2018 - full year data expected | 11.97 | 22 | 95
South West Water | MEAVY WASTEWATER TREATMENT WORKS | MEAVY S T STW_SO_DOUSLAND | 301942 | 301942 | A2 | Inlet SO at WwTW | SX 5394 6717 | GB108047003660 | Meavy | RIVER MEAVY (S) |  |  | EDM to be installed by December 2023
South West Water | MEETH STW | MEETH STW_SSO_MEETH | NRA-SW-0003 | NRA-SW-0003 | A2 | Storm tank at WwTW | SS 5458 0795 | GB108050014190 | Little Mere River | UNNAMED WATERCOURSE |  |  | EDM to be installed by December 2023
South West Water | #TBC | MENAGWINS STW_SO_ST AUSTELL | #TBC | in progress | tbc | Inlet SO at WwTW | SX 01158 50953 | GB108048002280 | St Austell River | #TBC |  |  | EDM to be installed by December 2023
South West Water | ST AUSTELL WWTW (MENAGWINS) | MENAGWINS STW_SSO_ST AUSTELL | 31294 | 31294 | A2 | Storm tank at WwTW | SX 0117 5096 | GB108048002280 | St Austell River | ST AUSTELL RIVER |  | PENTEWAN BEACH | Commissioned pre-2016 - full year data expected | 1197.86 | 94 | 100 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue
South West Water | MENHENIOT WWTW | MENHENIOT STW_SSO_MENHENIOT | 15/48/171/P/3A | 15/48/171/P/3 | A2 | Storm tank at WwTW | SX 2843 6203 | GB108048002320 | Seaton | TRIBUTARY OF THE RIVER SEATON |  | SEATON BEACH (CORNWALL) | Commissioned pre-2016 - full year data expected | 728.42 | 59 | 100
South West Water | MULLION TRANSFER PS | MERES VALLEY SPST_PSCSOEO_MULLION | 302947 | 302947 | A1 | Storm discharge at pumping station | SW 6651 1902 | 269 | #N/A | POLURRIAN COVE (C) |  | POLURRIAN COVE BEACH | Commissioned in 2017 - full year data expected | 40.29 | 23 | 100
South West Water | METHERELL WWTW | METHERELL STW_SO_METHERELL | NRA-SW-4999 | NRA-SW-4999 | A2 | Inlet SO at WwTW | SX 4106 6927 | GB108047004070 | Cotehele Stream | TRIBUTARY OF RIVER TAMAR |  |  | Commissioned in 2019 - full year data expected | 58.58 | 14 | 100
South West Water | METHERELL WWTW | METHERELL STW_SSO_METHERELL | NRA-SW-4999 | NRA-SW-4999 | A3 | Storm tank at WwTW | SX 4106 6927 | GB108047004070 | Cotehele Stream | TRIBUTARY OF RIVER TAMAR |  |  | Commissioned in 2019 - full year data expected | 3648.41 | 166 | 100
South West Water | MEVAGISSEY PS | MEVAGISSEY SPST_PSCSOEO_MEVAGISSEY | 300238/PC/01 | 300238/PC/01 | A1 | Storm discharge at pumping station | SX 0180 4494 | 256 | #N/A | MEVAGISSEY BAY |  | POLSTREATH BEACH | Commissioned pre-2016 - full year data expected | 90.88 | 127 | 100
South West Water | MIDDLE MARWOOD WWTW | MIDDLE MARWOOD STW_SO_MARWOOD | 203312 | 203312 | A2 | Inlet SO at WwTW | SS 5373 3766 | GB108050020020 | Knowl Water | KNOWLE WTER & MID MARWOOD STRM |  |  | Commissioned in 2017 - full year data expected | 250.55 | 34 | 100
South West Water | MIDDLE MARWOOD WWTW | MIDDLE MARWOOD STW_SSO_MARWOOD | 203312 | 203312 | A3 | Storm tank at WwTW | SS 5332 3739 | GB108050020020 | Knowl Water | KNOWLE WTER & MID MARWOOD STRM |  |  | Commissioned in 2018 - full year data expected | 2031.07 | 92 | 100
South West Water | MIDDLE MARWOOD WWTW | MIDDLE MARWOOD STW_SSO_MARWOOD | 203312 | 203312 | A3 | Storm tank at WwTW | SS 5331 3739 | GB108050020020 | Knowl Water | KNOWLE WTER & MID MARWOOD STRM |  |  | Commissioned in 2018 - full year data expected | 2031.07 | 92 | 100
South West Water | MIDDLE MILL LANE CSO | MIDDLE MILL LN_CSO_CULLOMPTON | 201859 | 201859 | A1 | SO on sewer network | ST 0228 0735 | GB108045014970 | Lower Culm | MILL LEAT |  |  | Commissioned in 2019 - full year data expected | 0.3 | 2 | 100
South West Water | R/O 68 WOOLBROOK ROAD CSO | MIDDLE WOOLBROOK_CSO_WOOLBROOK | 201829 | 201829/CS/01 | A1 | SO on sewer network | SY 1235 8912 | GB108045009160 | Sid | WOOLBROOK (S) |  |  | EDM to be installed by December 2023
South West Water | MILLBAY TANKS | MILBAY STORAGE TANK_CSOEO_PLYMOUTH | 300820 | 300820 | A1 | SO on sewer network | SX 4718 5357 | 73 | #N/A | PLYMOUTH SOUND(E) |  | PLYMOUTH HOE (WEST) | Commissioned pre-2016 - full year data expected | 7.55 | 1 | 51 | Comms failure / issue | N/A - Ongoing investigation
South West Water | MILFORD PARK PUMPING STATION | MILFORD PARK SPST_PSCSOEO_TEIGNMOUTH | 201656 | 201656 | A1 | Storm discharge at pumping station | SX 9313 7296 | 22 | #N/A | RIVER TEIGN VIA SWS ESTUARINE | Teign | SHALDON BEACH | Commissioned pre-2016 - full year data expected | 2.05 | 2 | 100
South West Water | MILL CREEK PUMPING STATION | MILL CREEK SPS_PSCSOEO_DITTISHAM | 202742 | 202742 | A1 | Storm discharge at pumping station | SX 8593 5522 | 23 | #N/A | DITTISHAM MILL CREEK-ESTUARINE | Dart |  | Commissioned pre-2016 - full year data expected | 25.57 | 18 | 100
South West Water | MILL LANE CSO | MILL LN_CSO_UPLYME | 201817 | 201817 | A1 | SO on sewer network | SY 3312 9331 | GB108044009760 | Lim | RIVER LIM (S) |  | LYME REGIS CHURCH CLIFF BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | MILL RACE COMBINED SEWER OVERFLOW | MILL RACE/RIVER EXE_CSO_EXETER | 201896 | 201896 | A1 | SO on sewer network | SX 9341 9062 | GB108045009050 | North Brook (East Devon) | MILL RACE, RIVER EXE | Exe |  | Commissioned in 2018 - full year data expected | 104.5 | 32 | 100
South West Water | MILL ROAD PUMPING STATION | MILL ROAD SPS_PSCSOEO_EXETER | 201628 | 201628 | A1 | Storm discharge at pumping station | SX 9397 9012 | GB108045009050 | North Brook (East Devon) | RIVER EXE (ESTUARINE) | Exe |  | Commissioned in 2017 - full year data expected | 16.41 | 10 | 94
South West Water | MILL STREET COMBINED SEWER OVERFLOW | MILL ST_CSO_CREDITON | 201865 | 201865 | A1 | SO on sewer network | SS 8419 0030 | GB108045009090 | Middle Creedy | TRIB OF RIVER CREEDY VIA SWS |  |  | Commissioned in 2019 - full year data expected | 89.2 | 13 | 100
South West Water | MILLSTREET CSO | MILL ST_CSO_OTTERY | 201381 | 201381 | A1 | SO on sewer network | SY 0939 9511 | GB108045009170 | Lower River Otter | RIVER OTTER VIA SWS |  |  | Commissioned in 2019 - full year data expected | 13.55 | 12 | 100
South West Water | MILL BRIDGE CSO | MILLBRIDGE_CSO_PLYMOUTH | 301751 | 301751 | A1 | SO on sewer network | SX 4622 5441 | 73 | #N/A | STONEHOUSE CREEK VIA SWS (EST) |  |  | Commissioned pre-2016 - full year data expected | 8.76 | 11 | 100
South West Water | MILLBROOK STW | MILLBROOK STW_SSO_MILLBROOK | NRA-SW-7829/FN/1 | NRA-SW-7829 | A2 | Storm tank at WwTW | SX 4355 5229 | 72 | #N/A | MILLBROOK LAKE |  |  | Commissioned in 2019 - full year data expected | 699.5 | 59 | 100
South West Water | MILLMOOR LANE COMBINED SEWER OF | MILLMOOR LN_CSO_NEWTON POPPLEFORD | 201844 | 201844 | A1 | SO on sewer network | SY 0896 8961 | GB108045009170 | Lower River Otter | TRIB OF RIVER OTTER VIA SWS |  |  | Commissioned in 2020 - full year data expected | 10.77 | 15 | 88 | Sensor failure / issue | Resolved - February
South West Water | MILLMOOR CSO | MILLMOOR_CSO_CULMSTOCK | 202236 | 202236/CS/01 | A1 | SO on sewer network | ST 1007 1376 | GB108045014980 | Middle Culm | RIVER CULM(S) |  |  | EDM to be installed by December 2023
South West Water | MILTON ABBOT WWTW | MILTON ABBOT STW_SO_MILTON ABBOT | NRA-SW-3402 | NRA-SW-3402 | A2 | Inlet SO at WwTW | SX 4025 7919 | GB108047007860 | Lower River Tamar | TRIBUTARY OF THE RIVER TAMAR |  |  | Commissioned in 2018 - full year data expected | 599.21 | 90 | 100
South West Water | OLD BRIDGE STREET CAR PARK CSO | MITCHELL HILL_CSO_TRURO | NPSWQD006230 | NPSWQD006230 | A1 | SO on sewer network | SW 8279 4489 | 76 | #N/A | RIVER ALLEN | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | MITCHELL PUMPING STATION | MITCHELL SPST_PSCSOEO_TRURO | 302286 | 302286 | A1 | Storm discharge at pumping station | SW 8567 5486 | GB108049000210 | Benny Stream | BENNY STREAM(S) |  |  | EDM to be installed by December 2023
South West Water | MODBURY WASTEWATER TREATMENT WORKS | MODBURY STW_SSO_MODBURY | SWWA 2259 | SWWA 2259 | A2 | Storm tank at WwTW | SX 6537 5136 | GB108046005020 | Ayleston Brook | AYLESTON BROOK (S) |  | MOTHECOMBE BEACH | Commissioned pre-2016 - full year data expected | 411.26 | 67 | 100
South West Water | MOLINNIS COMBINED SEWER OVERFLOW | MOLINNIS_CSO_BUGLE | 301683 | 301683 | A1 | SO on sewer network | SX 0264 5936 | GB108048002310 | Par River (Upper) | TRIBUTARY OF RIVER PAR |  |  | Commissioned in 2019 - full year data expected | 53.87 | 38 | 95
South West Water | MOLLAND ( WEST ) STW | MOLLAND WEST STW_SO_MOLLAND | 202201/CS/01 | 202201/CS/01 | A2 | Inlet SO at WwTW | SS 8040 2830 | GB108050014140 | Yeo (Molland) | UNNAMED WATERCOURSE (S) |  |  | EDM to be installed by December 2023
South West Water | MONKERTON PUMPING STATION | MONKERTON SPS_PSCSOEO_EXETER | 201635 | 201635 | A1 | Storm discharge at pumping station | SX 9671 9397 | GB108045008860 | Upper Clyst | PIN BROOK |  |  | Commissioned in 2016 - full year data expected | 1.37 | 1 | 98
South West Water | MONKLEIGH SEWAGE TREATMENT WORKS | MONKLEIGH STW_SO_MONKLEIGH | DRA 1149 | DRA 1149 | A2 | Inlet SO at WwTW | SS 4582 2045 | GB108050014660 | Torridge (Lew to Estuary) | RIVER TORRIDGE |  |  | Commissioned in 2020 - full year data expected | 114.55 | 42 | 95
South West Water | MOON COVE CSO | MOON COVE NORTH YARD_CSO_PLYMOUTH | 301992 | 301992 | A1 | SO on sewer network | SX 4474 5536 | 73 | #N/A | HAMOAZE (ESTUARINE) |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 100
South West Water | MOORLAND ROAD CSO | MOORLAND RD_CSO_PLYMOUTH | 301703 | 301703 | A1 | SO on sewer network | SX 5409 5668 | GB108047003640 | Tory Brook | TORY BROOK (VIA SWS) |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | MOORLANDS PSCSO/EO | MOORLANDS IND ESTATE SPS_PSCSOEO_SALTASH | 300430/PE/01 | 300430/PE/01 | A1 | Storm discharge at pumping station | SX 4100 5996 | 71 | #N/A | RIVER LYNHER ESTUARY | Tamar |  | Commissioned pre-2016 - full year data expected | 2.11 | 9 | 70 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | MOREBATH STW | MOREBATH STW_SO_BAMPTON | 202202/CS/01 | 202202/CS/01 | A2 | Inlet SO at WwTW | SS 9535 2477 | GB108045015070 | Lower Batherm | SHUTTERN BROOK (S) |  |  | EDM to be installed by December 2023
South West Water | MORETON PARK ROAD CSO | MORETON PARK RD_CSO_BIDEFORD | 203119 | 203119 | A1 | SO on sewer network | SS 4392 2604 | GB108050014500 | Kenwith Stream | TRIBUTARY OF KENWITH (S) | Taw/Torridge |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 82 | Sensor failure / issue | Resolved - December
South West Water | MORETONHAMPSTEAD WWTW | MORETONHAMPSTEAD STW_SO_MORETONHAMPSTEAD | NRA-SW-3912 | NRA-SW-3912 | A2 | Inlet SO at WwTW | SX 7672 8503 | GB108046008330 | Wray Brook | THE WRAY BROOK |  |  | Commissioned in 2017 - full year data expected | 1162.4 | 93 | 100
South West Water | MORETONHAMPSTEAD WWTW | MORETONHAMPSTEAD STW_SSO_MORETONHAMPSTD | NRA-SW-3912 | NRA-SW-3912 | A3 | Storm tank at WwTW | SX 7672 8503 | GB108046008330 | Wray Brook | THE WRAY BROOK |  |  | Commissioned in 2017 - full year data expected | 2513.23 | 152 | 93
South West Water | MORICE YARD CSO | MORICE YARD_CSO_PLYMOUTH | 301991 | 301991 | A1 | SO on sewer network | SX 4478 5497 | 73 | #N/A | HAMOAZE (ESTUARINE) |  |  | Commissioned in 2017 - full year data expected | 0.21 | 2 | 100
South West Water | MORLAIX AVENUE (FYFFES SLIPWAY) CSO | MORLAIX AV_CSO_FYFFES SLIPWAY | 2894/22 | 2894/22 | A1 | SO on sewer network | SW 8288 4429 | 76 | #N/A | TRIB OF TRURO RIVER(ESTUARINE) | Fal Estuary |  | Commissioned in 2019 - full year data expected | 61.8 | 31 | 76 | Comms failure / issue | N/A - Ongoing investigation
South West Water | MOSTERTON PUMPING STATION | MOSTERTON SPS_PSCSOEO_MOSTERTON | 201546 | 201546 | A1 | Storm discharge at pumping station | ST 4575 0527 | GB108045014840 | Upper Axe | RIVER AXE |  |  | Commissioned in 2017 - full year data expected | 162.56 | 48 | 100
South West Water | MOUNT HOUSE SCHOOL PS | MOUNT HOUSE SPS_PSCSOEO_TAVISTOCK | 301640 | NRA-SW-0971 | A1 | Storm discharge at pumping station | SX 4918 7472 | GB108047007840 | Lower River Tavy | TRIB OF THE RIVER TAVY |  |  | Commissioned pre-2016 - full year data expected | 1.17 | 3 | 100
South West Water | MOUSEHOLE PUMPING STATION | MOUSEHOLE SPS_PSCSOEO_MOUSEHOLE | 301588 | 301588 | A1 | Storm discharge at pumping station | SW 4701 2617 | 405 | #N/A | MOUNTS BAY (COASTAL) |  |  | Commissioned in 2018 - full year data expected | 10.08 | 20 | 100
South West Water | MOWHAY ROAD NO.2 CSO | MOWHAY ROAD CSO_PLYMOUTH | 302616 | 302616 | A1 | SO on sewer network | SX 4609 5846 | 73 | #N/A | HONICKNOWLE STREAM | Tamar |  | Commissioned pre-2016 - full year data expected | 2.31 | 4 | 53 | Comms failure / issue | Resolved - July
South West Water | MOYLE ROAD CSO | MOYLE RD_CSO_PADSTOW | 302975 | 302975 | A1 | SO on sewer network | SW 9225 7478 | 135 | #N/A | CAMEL ESTUARY (E) | Camel | ROCK BEACH | Commissioned pre-2016 - full year data expected | 4.92 | 18 | 100
South West Water | MUDDIFORD PUMPING STATION | MUDDIFORD SPS_PSCSOEO_MUDDIFORD | 201617 | 201617 | A1 | Storm discharge at pumping station | SS 5630 3822 | GB108050020040 | Bradiford Water | COLAM STREAM |  |  | Commissioned in 2019 - full year data expected | 974.1 | 50 | 100
South West Water | MUDDLEBRIDGE CSO | MUDDLEBRIDGE_CSO_FREMINGTON | 203288 | 203288 | A1 | SO on sewer network | SS 5225 3249 | 198 | #N/A | BRYN BROOK(S) | Taw/Torridge |  | Commissioned pre-2016 - full year data expected | 420.68 | 34 | 100
South West Water | MUSBURY & WHITFORD STW | MUSBURY & WHITFORD STW_SO_WHITFORD | NRA-SW-6684 | NRA-SW-6684 | A2 | Inlet SO at WwTW | SY 2624 9507 | GB108045008870 | Lower Axe | (S) RIVER AXE |  |  | Commissioned in 2020 - full year data expected | 326.01 | 85 | 100
South West Water | MUTTON COVE PUMPING STATION | MUTTON COVE SPS_PSCSOEO_PLYMOUTH | 300824 | 300824 | A1 | Storm discharge at pumping station | SX 4529 5395 | 73 | #N/A | RIVER TAMAR (ESTUARINE) |  |  | Commissioned in 2016 - full year data expected | 65.75 | 45 | 100
South West Water | MYLOR BRIDGE WWTW | MYLOR STW_SO_MYLOR BRIDGE | 302505 | 302505 | A2 | Inlet SO at WwTW | SW 7993 3638 | 76 | #N/A | MYLOR CREEK | Fal Estuary |  | Commissioned in 2016 - full year data expected | 145.8 | 179 | 100
South West Water | MYLOR BRIDGE WWTW | MYLOR STW_SSO_MYLOR BRIDGE | 302505 | 302505 | A3 | Storm tank at WwTW | SW 7993 3638 | 76 | #N/A | MYLOR CREEK | Fal Estuary |  | Commissioned in 2016 - full year data expected | 911.28 | 85 | 100
South West Water | BROOK COTTAGE PUMPING STATION | NADDERWATER SPS_PSCSOEO_WHITESTONE | 301667 | 301667 | A1 | Storm discharge at pumping station | SX 8911 9344 | GB108045009020 | Alphin Brook | NADDER BROOK | Exe |  | Commissioned in 2016 - full year data expected | 367.24 | 65 | 100
South West Water | NANCHERROW HILL CSO | NANCHERROW HILL_CSO_ST JUST | 301815 | 301815/CS/01 | A1 | SO on sewer network | SW 3693 3191 | 230 | #N/A | LOCAL STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | NANNY MOORES BRIDGE CSO | NANNY MOORES BRIDGE_CSO_BUDE | 301689 | 301689/CS/01 | A1 | SO on sewer network | SS 2082 0641 | GB108049007280 | Lower River Strat | RIVER NEET (S) |  | SUMMERLEAZE | Commissioned pre-2016 - full year data expected | 1.62 | 1 | 88 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | NANSLADRON PUMPING STATION | NANSLADRON SPST_PSCSOEO_ST AUSTELL | 302111 | 302111 | A1 | Storm discharge at pumping station | SX 0071 4825 | GB108048002280 | St Austell River | TRIBUTARY OF WHITE RIVER |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 100
South West Water | BODMIN NANSTALLON WWTW | NANSTALLON STW_SSO_BODMIN | NRA-SW-6959 | NRA-SW-6959 | A2 | Storm tank at WwTW | SX 0433 6735 | GB108049000190 | Lower River Camel | RIVER CAMEL/ST LAWRENCE STR | Camel |  | Commissioned pre-2016 - full year data expected | 942.91 | 56 | 100
South West Water | NEW PARK (GARDEN) CSO | NEW PARK GARDEN_CSO_WIDECOMBE | 201693 | 201693/CS/01 | A1 | SO on sewer network | SX 7175 7661 | GB108046008390 | East Webburn River | STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | NEW POLZEATH PUMPING STATION | NEW POLZEATH SPS_PSCSOEO_POLZEATH | 34547 | 034547/PC/01 | A1 | Storm discharge at pumping station | SW 9346 7957 | 135 | #N/A | (E) POLZEATH BAY |  | POLZEATH BEACH | Commissioned pre-2016 - full year data expected | 4.42 | 1 | 100
South West Water | NEW ROAD CSO | NEW ROAD_CSO_LISKEARD | 303469 | 303469 | A1 | SO on sewer network | SX 2403 6412 | GB108048001440 | East Looe River | TRIBUTARY OF EAST LOOE RIVER |  | EAST LOOE BEACH | Commissioned pre-2016 - full year data expected | 159.57 | 27 | 89 | Comms failure / issue | Resolved - February
South West Water | NEWHAM ROAD PUMPING STATION | NEWHAM ROAD SPST_PSCSOEO_TRURO | 303468 | 303468 | A1 | Storm discharge at pumping station | SW 8297 4416 | 76 | #N/A | TRURO RIVER (ESTUARINE) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 9.62 | 14 | 100
South West Water | TRURO (NEWHAM) STW | NEWHAM STW_SSO_TRURO | 302707 | 302707 | A2 | Storm tank at WwTW | SW 8341 4329 | 76 | #N/A | TRURO RIVER ESTUARY(E) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 300.39 | 25 | 100
South West Water | ST NEWLYN EAST WWTW | NEWLYN EAST STW_SO_NEWLYN EAST | NRA-SW-6625 | NRA-SW-6625 | A2 | Inlet SO at WwTW | SW 8293 5688 | GB108049000220 | Gannel (Lower) | RIVER GANNEL |  |  | Commissioned in 2020 - full year data expected | 24.68 | 39 | 100
South West Water | NEWNHAM ROAD CSO | NEWNHAM ROAD_CSO_COLEBROOK | 301756 | 301756 | A1 | SO on sewer network | SX 5423 5683 | GB108047003640 | Tory Brook | TORY BROOK VIA SWS |  |  | Commissioned in 2018 - full year data expected | 33.27 | 43 | 100
South West Water | NEWPORT PARK PUMPING STATION | NEWPORT PARK SPS_PSCSOEO_EXETER | 201631 | 201631 | A1 | Storm discharge at pumping station | SX 9541 8899 | 19 | #N/A | TRIB OF RIVER EXE (ESTUARINE) | Exe |  | Commissioned in 2016 - full year data expected | 0 | 0 | 100
South West Water | NEWPORT INDUSTRIAL ESTATE CSO | NEWPORT_CSO_LAUNCESTON | 301850 | 301850 | A1 | SO on sewer network | SX 3351 8492 | GB108047007960 | Kensey | RIVER KENSEY |  |  | Commissioned in 2016 - full year data expected | 1176.34 | 139 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
South West Water | NORTH FAL STW (ST STEPHENS COOMBE) | NORTH FAL STW_SO_ST STEVENS | 302298 | 302298 | A2 | Inlet SO at WwTW | SW 9412 5092 | GB108048001350 | Gwindra Stream | GWINDRA STREAM (S) |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 100
South West Water | NORTH FAL STW (ST STEPHENS COOMBE) | NORTH FAL STW_SSO_ST STEVENS | 302298 | 302298 | A2 | Storm tank at WwTW | SW 9412 5092 | GB108048001350 | Gwindra Stream | GWINDRA STREAM (S) |  |  | Commissioned in 2018 - full year data expected | 215.84 | 32 | 100
South West Water | NORTH HILL WWTW | NORTH HILL STW_SO_NORTH HILL | NRA-SW-6621 | NRA-SW-6621 | A2 | Inlet SO at WwTW | SX 2703 7631 | GB108047007670 | Lower River Lynher | RIVER LYNHER |  |  | Commissioned in 2018 - full year data expected | 349.04 | 132 | 100
South West Water | NORTH LAWN COURT CSO | NORTH LAWN CT_CSO_EXETER | 201911 | 201911 | A1 | SO on sewer network | SX 9479 9230 | GB108045009050 | North Brook (East Devon) | NORTH BROOK VIA SWS | Exe |  | Commissioned in 2018 - full year data expected | 1.43 | 10 | 52 | Comms failure / issue | Resolved - September
South West Water | CSO OFF PENDARVES ROAD | NORTH PARADE_CSO_FALMOUTH | 303010 | 303010 | A1 | SO on sewer network | SW 7989 3392 | 402 | #N/A | PENRYN RIVER | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 14.39 | 28 | 100
South West Water | NORTH PETHERWIN WWTW | NORTH PETHERWIN STW_SO_NORTH PETHERWIN | NRA-SW-3765 | NRA-SW-3765 | A2 | Inlet SO at WwTW | SX 2939 8782 | GB108047007981 | Lower River Ottery | RIVER OTTERY |  |  | Commissioned in 2018 - full year data expected | 587.05 | 104 | 92 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP7 or Green Recovery
South West Water | NORTH PETHERWIN PSCSO/EO | NORTH PETHERWIN_PSCSOEO_LAUNCESTON | 301623 | 301623/PC/01 | A1 | Storm discharge at pumping station | SX 2829 8862 | GB108047007800 | Bolesbridge Water | RIVER OTTERY (S) |  |  | EDM to be installed by December 2023
South West Water | CAMELS HEAD WWTW | NORTH PROSPECT_CSO_PLYMOUTH | 302613 | 302613 | A1 | SO on sewer network | SX 4466 5714 | 73 | #N/A | WESTON MILL LAKE(E) | Tamar |  | Commissioned pre-2016 - full year data expected | 2.68 | 4 | 100
South West Water | NORTH SANDS PUMPING STATION | NORTH SANDS SPST_PSCSOEO_SALCOMBE | NRA-SW-7655/PC/1 | NRA-SW-7655 | A1 | Storm discharge at pumping station | SX 7300 3822 | 430 | #N/A | TRIB OF KINGSBRIDGE ESTUARY |  | SALCOMBE NORTH SANDS | Commissioned pre-2016 - full year data expected | 2.05 | 4 | 100
South West Water | NORTH STREET CAR PARK CSO | NORTH ST CAR PARK_CSO_CREDITON | 201872 | 201872 | A1 | SO on sewer network | SS 8448 0041 | GB108045009090 | Middle Creedy | TRIB OF RIVER CREEDY VIA SWS |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 100
South West Water | NORTH STREET CSO | NORTH ST_CSO_OKEHAMPTON | 201729 | 201729 | A1 | SO on sewer network | SX 5880 9544 | GB108050008100 | East Okemont River | TRIB OF EAST OKEMENT RIVER |  |  | Commissioned in 2018 - full year data expected | 107.1 | 60 | 100
South West Water | NORTH TAWTON WWTW | NORTH TAWTON STW_SO_NORTH TAWTON | NRA-SW-0005 | NRA-SW-0005 | A2 | Inlet SO at WwTW | SS 6546 0196 | GB108050008250 | Taw (Source to Bullow Brook) | RIVER TAW |  |  | Commissioned in 2017 - full year data expected | 48.39 | 72 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
South West Water | NORTH TAWTON WWTW | NORTH TAWTON STW_SSO_NORTH TAWTON | NRA-SW-0005 | NRA-SW-0005 | A2 | Storm tank at WwTW | SS 6546 0196 | GB108050008250 | Taw (Source to Bullow Brook) | RIVER TAW |  |  | Commissioned in 2017 - full year data expected | 1121.59 | 87 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
South West Water | NORTHAM WASTE WATER PUMPING STATION | NORTHAM FSCN SPS _PSEO_BIDEFORD | 2878 | 2878 | A2 | Storm discharge at pumping station | SS 4193 2919 | 236 | #N/A | BIDEFORD BAY & THE PILL |  | WESTWARD HO! BEACH | Commissioned pre-2016 - full year data expected | 11.04 | 12 | 100
South West Water | NORTHAM WASTE WATER PUMPING STATION | NORTHAM GOLF LINKS ROAD_SPS_BIDEFORD | 2878 | 2878 | A1 | Storm discharge at pumping station | SS 4401 2977 | 236 | #N/A | BIDEFORD BAY & THE PILL |  | INSTOW BEACH | Commissioned in 2017 - full year data expected | 87.73 | 59 | 100
South West Water | NORTHBROOK GOLF COURSE LOWER CSO | NORTHBROOK GOLF COURSE (LOWER_CSO_EXETER | 201897 | 201897 | A1 | SO on sewer network | SX 9382 9039 | GB108045009050 | North Brook (East Devon) | NORTHBROOK | Exe |  | Commissioned in 2017 - full year data expected | 45.45 | 18 | 88 | Comms failure / issue | Resolved - April
South West Water | NORTHBROOK PARK GOLF CRSE UPPER CSO | NORTHBROOK GOLF COURSE UPPER_CSO_EXETER | 201914 | 201914 | A1 | SO on sewer network | SX 9383 9040 | GB108045009050 | North Brook (East Devon) | NORTHBROOK | Exe |  | Commissioned in 2017 - full year data expected | 43.11 | 23 | 100
South West Water | NOSS MAYO PUMPING STATION | NOSS MAYO SPST_PSCSOEO_NEWTON FERRERS | 301659 | 301659 | A1 | Storm discharge at pumping station | SX 5512 4788 | 70 | #N/A | NEWTON CREEK (ESTUARINE) | Yealm |  | Commissioned in 2016 - full year data expected | 0 | 0 | 100
South West Water | HIGHER COOMBE DRIVE CSO | O/S 45 HIGHER COOMBE DR_CSO_TEIGNMOUTH | 201701 | 201701 | A1 | SO on sewer network | SX 9315 7403 | 22 | #N/A | BITTON BROOK VIA SWS | Teign |  | Commissioned in 2018 - full year data expected | 0 | 0 | 100
South West Water | ST THOMAS STREET CSO | O/S 58 THOMAS ST_CSO_PENRYN | 303478 | 303478 | A1 | SO on sewer network | SW 7861 3422 | 402 | #N/A | TRIB OF PENRYN RIVER(S) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 27.92 | 24 | 91
South West Water | OAKFORD STW | OAKFORD STW_SO_OAKFORD | 202204/CS/01 | 202204/CS/01 | A2 | Inlet SO at WwTW | SS 9115 2142 | GB108045015040 | Iron Mill Stream | TRIB OF IRON MILL STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | OAKLAND PARK CSO | OAKLAND PARK_CSO_BARNSTAPLE | 203160 | 203160 | A1 | SO on sewer network | SS 5463 3289 | 198 | #N/A | RIVER TAW ESTUARY(E) | Taw/Torridge |  | Commissioned pre-2016 - full year data expected | 1.69 | 16 | 100
South West Water | OAKLANDS CSO | OAKLANDS_CSO_PETROCKSTOWE | 201944 | 201944/CS/01 | A1 | SO on sewer network | SS 5130 0983 | GB108050014190 | Little Mere River | TRIB OF LITTLE MERE RIVER (S) |  |  | EDM to be installed by December 2023
South West Water | OCEAN COURT PUMPING STATION | OCEAN COURT SPS_PSCSOEO_PLYMOUTH | 300823 | 300823 | A1 | Storm discharge at pumping station | SX 4583 5385 | 73 | #N/A | PLYMOUTH SOUND (ESTUARINE) |  |  | Commissioned pre-2016 - full year data expected | 84.83 | 39 | 100
South West Water | EBFORD PUMPING STATION | ODHAMS WHARF SPS_PSCSOEO_EBFORD | 202365 | 202365 | A1 | Storm discharge at pumping station | SX 9758 8794 | GB108045008750 | Lower Clyst | RIVER CLYST (ESTUARINE) | Exe |  | Commissioned in 2016 - full year data expected | 703.69 | 261 | 100 |  |  | Data collection - Tidal / river inundation | N/A - Ongoing investigation | N/A - Operational solution applied
South West Water | OKEHAMPTON ROAD CSO | OKEHAMPTON RD_CSO_EXETER | 201903 | 201903 | A1 | SO on sewer network | SX 9299 9067 | 19 | #N/A | RIVER EXE VIA SWS | Exe |  | Commissioned in 2018 - full year data expected | 0.81 | 3 | 98
South West Water | OLD FERRY ROAD CSO | OLD FERRY ROAD_CSO_SALTASH | 302587 | 302587 | A1 | SO on sewer network | SX 4329 5912 | 71 | #N/A | TAMAR ESTUARY(E) | Tamar |  | Commissioned in 2016 - full year data expected | 9.13 | 15 | 100
South West Water | OLD GATEWAY 1 COMBINED SEWER OF | OLD GATEWAY 1_CSO_OKEHAMPTON | 201727 | 201727 | A1 | SO on sewer network | SX 5883 9528 | GB108050008100 | East Okemont River | EAST OKEMENT RIVER |  |  | Commissioned in 2016 - full year data expected | 36.33 | 46 | 100
South West Water | OLD GATEWAY 2 COMBINED SEWER OF | OLD GATEWAY 2_CSO_OKEHAMPTON | 201726 | 201726 | A1 | SO on sewer network | SX 5884 9527 | GB108050008100 | East Okemont River | EAST OKEMENT RIVER |  |  | Commissioned in 2019 - full year data expected | 9.6 | 21 | 100
South West Water | OLD HILL PS | OLD HILL SPS_PSCSOEO_FALMOUTH | 303008 | 303008 | A1 | Storm discharge at pumping station | SW 7973 3371 | 402 | #N/A | PENRYN RIVER(E) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 20.12 | 13 | 100
South West Water | OLD HILL (TRESAWLE RD) CSO | OLD HILL_CSO_FALMOUTH | 303009 | 303009 | A1 | SO on sewer network | SW 7973 3371 | 402 | #N/A | PENRYN RIVER(E) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | OLD JAIL COMBINED SEWER OVERFLOW | OLD JAIL_CSO_BODMIN | 301827 | 301827 | A1 | SO on sewer network | SX 0580 6743 | GB108049000190 | Lower River Camel | BODMIN TOWN LEAT | Camel |  | Commissioned in 2020 - full year data expected | 2023.93 | 116 | 87 | Comms failure / issue | Resolved - April
South West Water | OLD MILL ROAD | OLD MILL RD_CSO_TORQUAY | 200230 | 200230 | A1 | SO on sewer network | SX 9022 6316 | 429 | #N/A | COCKINGTON STREAM TO SEA |  | TORRE ABBEY BEACH | Commissioned pre-2016 - full year data expected | 35.78 | 21 | 100
South West Water | OLD MILL PS | OLD MILL SPST_PSCSOEO_STOKE CLIMSLAND | 302112 | 302112 | A1 | Storm discharge at pumping station | SX 3698 7385 | GB108047007860 | Lower River Tamar | ALREN STREAM |  |  | Commissioned in 2019 - full year data expected | 1.5 | 3 | 100
South West Water | EXETER COLLEGE CSO | OLD SMITHY NORTH ROAD_CSO_OKEHAMPTON | 201375 | 201725 | A1 | SO on sewer network | SX 5886 9559 | GB108050008110 | Middle River Okement | HIGHER LEAT VIA SW SEWER |  |  | Commissioned in 2017 - full year data expected | 2 | 12 | 100
South West Water | OLD TOTNES ROAD CSO | OLD TOTNES RD_CSO_NEWTON ABBOT | 201737 | 201737 | A1 | SO on sewer network | SX 8534 7051 | GB108046008450 | Lemon | TRIB OF RIVER LEMON | Teign |  | Commissioned in 2019 - full year data expected | 0.3 | 4 | 88 | Comms failure / issue | Resolved - April
South West Water | OLD WOODBURY SALTERTON STW CSO | OLD WOODBURY SALTERTON STW_CSO_WOODBURY | NRA-SW-0271 | NRA-SW-0271 | A1 | SO on sewer network | SY 0128 8934 | GB108045008710 | Grindle Brook | TRIB OF GRINDLE BROOK VIA SWS | Exe |  | Commissioned in 2018 - full year data expected | 20.3 | 7 | 99
South West Water | OLD WOOLLEN MILL CSO | OLD WOOLLEN MILL_CSO_BUCKFASTLEIGH | 201803 | 201803 | A1 | SO on sewer network | SX 7421 6715 | GB108046008350 | Dart | RIVER DART |  |  | Commissioned in 2019 - full year data expected | 6.77 | 10 | 100
South West Water | HONDA GARAGE CSO | OPP 447 WOLSELEY RD_CSO_PLYMOUTH | 302610 | 302610 | A1 | SO on sewer network | SX 4519 5748 | 73 | #N/A | WESTON MILL STREAM(E) | Tamar |  | Commissioned pre-2016 - full year data expected | 220.69 | 26 | 56 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | ORESTON QUAY (NO 2) PUMPING STATION | ORESTON QUAY SPST_PSCSOEO_PLYMOUTH | 032898/PC/01 | 32898 | A1 | Storm discharge at pumping station | SX 5000 5351 | 73 | #N/A | RIVER PLYM ESTUARY (ESTUARINE) |  | PLYMOUTH HOE (EAST & WEST) | Commissioned pre-2016 - full year data expected | 35.55 | 25 | 100
South West Water | OTTERY ST MARY ATTENUATION TANK | OTTERY ST MARY ATTEN TANK_SO_OTTERY | DRA 96 | DRA 96 | A2 | SO on sewer network | SY 0947 9510 | GB108045009170 | Lower River Otter | THE RIVER OTTER |  |  | Commissioned in 2019 - full year data expected | 91.53 | 10 | 100
South West Water | OUTER HOPE PUMPING STATION | OUTER HOPE COVE SPST_PSCSOEO_HOPE COVE | 202605 | 202605 | A1 | Storm discharge at pumping station | SX 6739 4001 | 266 | #N/A | HOPE COVE (C) |  | HOPE COVE BEACH | Commissioned pre-2016 - full year data expected | 537.15 | 75 | 100
South West Water | OXEN COVE ATTENUATION TANK CSO | OXEN COVE SPST_PSCSOEO_BRIXHAM | 200524 | 200524/CS/01 | A1 | Storm discharge at pumping station | SX 9250 5658 | 429 | #N/A | BRIXHAM OUTER HARBOUR(C) | Brixham |  | Commissioned pre-2016 - full year data expected | 159.31 | 32 | 100
South West Water | PACK O CARDS | PACK OF CARDS_CSO_COMBE MARTIN | 2676 | 2676 | A1 | SO on sewer network | SS 5833 4667 | GB108051020440 | Umber | RIVER UMBER (S) |  | COMBE MARTIN BEACH | Commissioned pre-2016 - full year data expected | 86.5 | 14 | 100
South West Water | PADSTOW FORESHORE PUMPING STATION | PADSTOW FORESHORE SPST_PSCSOEO_PADSTOW | 302974 | 302974 | A1 | Storm discharge at pumping station | SW 9224 7492 | 135 | #N/A | RIVER CAMEL ESTUARY (E) | Camel | ROCK BEACH | Commissioned pre-2016 - full year data expected | 151.74 | 23 | 100
South West Water | PADSTOW HARBOUR PUMPING STATION | PADSTOW HARBOUR SPS_PSCSOEO_PADSTOW | 302973 | 302973 | A1 | Storm discharge at pumping station | SW 9201 7545 | 135 | #N/A | CAMEL ESTUARY (E) | Camel | ROCK BEACH | Commissioned pre-2016 - full year data expected | 8.1 | 13 | 100
South West Water | PAIGNTON GREEN TANK PSCSO/EO | PAIGNTON TANK_CSO_PAIGNTON | 200240 | 200240 | A1 | SO on sewer network | SX 8984 6036 | 429 | #N/A | PAIGNTON SANDS(C) |  | PAIGNTON (PAIGNTON SANDS) | Commissioned pre-2016 - full year data expected | 2.8 | 7 | 100
South West Water | PAR SEWAGE TREATMENT WORKS | PAR STW_SSO_ST AUSTELL | 031299/SS/01 | 031299/SS/01 | A2 | Storm tank at WwTW | SX 0662 5088 | 256 | #N/A | (C) ST AUSTELL BAY |  | SHORTHORN BEACH | Commissioned pre-2016 - full year data expected | 141.1 | 10 | 100
South West Water | PARADISE ROAD (GRAVEYARD) CSO | PARADISE RD GRAVEYARD_CSO_PLYMOUTH | 301758 | 301758 | A1 | SO on sewer network | SX 4622 5441 | 73 | #N/A | STONEHOUSE CREEK VIA SWS (EST) |  |  | Commissioned in 2016 - full year data expected | 20.72 | 10 | 29 | Comms failure / issue | Resolved - September
South West Water | PARK HILL CSO | PARK HILL/ALEXANDRA TERR_CSO_TEIGNMOUTH | 203089 | 203089 | A1 | SO on sewer network | SX 9355 7296 | 22 | #N/A | SURFACE WATER SEWER (S) | Teign |  | Commissioned pre-2016 - full year data expected | 1.51 | 4 | 100
South West Water | PARKLAND DRIVE PUMPING STATION | PARKLAND DRIVE SPS_PSCSOEO_EXETER | 201632 | 201632 | A1 | Storm discharge at pumping station | SX 9430 9124 | GB108045009050 | North Brook (East Devon) | NORTHBROOK VIA SWS | Exe |  | Commissioned in 2016 - full year data expected | 0 | 0 | 100
South West Water | PARSONAGE LANE PSCO/EO | PARSONAGE LANE SPS_PSCSOEO_SOUTH MOLTON | 202169 | 202169/PC/01 | A1 | Storm discharge at pumping station | SS 7148 2621 | GB108050014130 | Mole (Yeo to Burcombe Stream) | WATERCOURSE(S) |  |  | EDM to be installed by December 2023
South West Water | PATHFINDER TERMINAL PS | PATHFINDER SPST_PSCSOEO_TEDBURN ST MARY | 203479 | 203479 | A1 | Storm discharge at pumping station | SX 8248 9395 | GB108045009220 | Culvery River | LILLY BROOK(S) |  |  | Commissioned pre-2016 - full year data expected | 61.34 | 12 | 100
South West Water | PAULS TERRACE CSO | PAULS TERRACE_CSO_TRURO | 302676 | 302676 | A1 | SO on sewer network | SW 8255 4513 | GB108048002330 | Lower River Allen (Fal) | RIVER ALLEN | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 148.33 | 17 | 76 | Comms failure / issue | N/A - Ongoing investigation
South West Water | PAVILION PUMPING STATION | PAVILIONS SPST_PSCSOEO_IVYBRIDGE | 202170 | 202170 | A1 | Storm discharge at pumping station | SX 6319 5558 | GB108046005200 | Erme | RIVER ERME |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 100
South West Water | PEAR TREE CROSS CSO | PEAR TREE CROSS_CSO_ASHBURTON | 201952 | 201952/CS/01 | A1 | SO on sewer network | SX 7508 6928 | GB108046005270 | Ashburn | RIVER ASHBURTON (S) |  |  | EDM to be installed by December 2023
South West Water | PELYNT WASTEWATER TREATMENT WORKS | PELYNT STW_SSO_PELYNT | NRA-SW-4009 | NRA-SW-4009 | A2 | Storm tank at WwTW | SX 2014 5488 | GB108048001980 | Polperro River | TRIBUTARY OF RIVER POL |  |  | Commissioned in 2020 - full year data expected | 1981.61 | 122 | 100
South West Water | PENBOTHIDNO CSO | PENBOTHIDNO ESTATE_CSO_CONSTANTINE | 302789 | 302789 | A1 | SO on sewer network | SW 7366 2886 | GB108048001870 | Lestraines River | POLWHEVERAL STREAM(S) | Helford |  | Commissioned pre-2016 - full year data expected | 2.23 | 7 | 100
South West Water | PENNANCE MILL TIDAL TANKS CSO | PENNANCE MILL_CSO_FALMOUTH | 302305 | 302305/CS/01 | A1 | SO on sewer network | SW 7894 3058 | 403 | #N/A | MAENPORTH STREAM(S) |  | MAENPORTH BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | PENNSYLVANIA ROAD CSO | PENNSYLVANIA ROAD_CSO_EXETER | 201372 | 201372 | A1 | SO on sewer network | SX 9147 9250 | GB108045009040 | Exe (Creedy to Estuary) | HIGHER LEAST VIA SW SEWER | Exe |  | Commissioned in 2017 - full year data expected | 89.77 | 35 | 100
South West Water | PENNYCOMEQUICK HILL CSO | PENNYCOMEQUICK HILL_CSO_PLYMOUTH | 303406 | 303406 | A1 | SO on sewer network | SX 4622 5441 | 73 | #N/A | STONE HOUSE CREEK VIA SWS |  |  | Commissioned in 2016 - full year data expected | 0.71 | 8 | 83 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | PENNYCOMEQUICK ROUNDABOUT CSO | PENNYCOMEQUICK ROUNDABOUT_CSO_PLYMOUTH | 301717 | 301717 | A1 | SO on sewer network | SX 4622 5441 | 73 | #N/A | PLYMOUTH SOUND VIA SWS |  |  | Commissioned pre-2016 - full year data expected | 5.39 | 9 | 94
South West Water | PENNYMOOR SEWAGE TREATMENT WORKS | PENNYMOOR STW_SO_TIVERTON | 203846 | 203846 | A2 | Inlet SO at WwTW | SS 8645 1163 | GB108045014910 | Upper Creedy | A TRIBUTARY OF BINNEFORD WATER |  |  | EDM to be installed by December 2023
South West Water | MILL ROAD PSCSO/EO | PENPONDS SPS_PSCSOEO_CAMBORNE | 301602 | 301602/PC/01 | A1 | Storm discharge at pumping station | SW 6304 3906 | GB108049000560 | Roseworthy Stream | RED RIVER (S) |  |  | EDM to be installed by December 2023
South West Water | PENPONT VIEW CSO | PENPONT VIEW_CSO_ALTARNUN | EPRYB3493NZ | EPR/YB3493NZ | A1 | SO on sewer network | SX 2244 8079 | GB108047007700 | Penpont Water | TRIBUTARY OF MILL LEAT |  |  | EDM to be installed by December 2023
South West Water | PENSILVA PUMPING STATION | PENSILVA SPST_PSCSOEO_PENSILVA | 303531 | 303531 | A1 | Storm discharge at pumping station | SX 2897 6881 | GB108047003890 | Tiddy | TRIBUTARY OF THE RIVER TIDDY |  |  | Commissioned in 2018 - full year data expected | 148.04 | 18 | 100
South West Water | PENCEPOOL FARM PUMPING STATION | PENSPOOL SPS_PSCSOEO_PLYMTREE | 201399 | 201399/PC/01 | A1 | Storm discharge at pumping station | ST 0522 0309 | GB108045008860 | Upper Clyst | TRIBUTARY OF RIVER CLYST (S) |  |  | Commissioned in 2020 - full year data expected | 41.33 | 11 | 100
South West Water | PENTEWAN PSCSO/EO | PENTEWAN SPS_PSCSOEO_ST AUSTELL | 302113 | 302113/PC/01 | A1 | Storm discharge at pumping station | SX 0196 4725 | 256 | #N/A | ST AUSTELL RIVER (S) |  | PENTEWAN BEACH | Commissioned pre-2016 - full year data expected | 145.31 | 8 | 100
South West Water | PERRANUTHNOE PUMPING STATION | PERRANUTHNOE SPS_PSCSOEO_MARAZION | 300828 | 300828/PC/01 | A1 | Storm discharge at pumping station | SW 5352 2914 | 405 | #N/A | (C) MOUNTS BAY |  | PERRANUTHNOE | Commissioned pre-2016 - full year data expected | 878.31 | 69 | 90
South West Water | PERRY STREET CSO | PERRY ST_CSO_TATWORTH | 201826 | 201826/CS/01 | A1 | SO on sewer network | ST 3360 0537 | GB108045014820 | Forton Brook | STREAM (S) |  |  | Commissioned in 2020 - full year data expected | 655.58 | 76 | 96
South West Water | PETERVILLE PUMPING STATION | PETERVILLE SPST_PSCSOEO_ST AGNES | 303458 | 303458 | A1 | Storm discharge at pumping station | SW 7214 5091 | 229 | #N/A | TREVAUNANCE STREAM(S) |  | TREVAUNANCE COVE BEACH | Commissioned pre-2016 - full year data expected | 166.37 | 32 | 100
South West Water | PEVERELL PARK ROAD CSO | PEVERELL PARK ROAD_CSO_PLYMOUTH | 301742 | 301742 | A1 | SO on sewer network | SX 4622 5441 | 73 | #N/A | STONEHOUSE CREEK VIA SWS (EST) |  |  | Commissioned pre-2016 - full year data expected | 18.73 | 37 | 100
South West Water | PHEAR PARK PSEO/CSO | PHEAR PARK SPST_PSCSOEO_EXMOUTH | 200124/PC/01 | 200124/PC/01 | A1 | Storm discharge at pumping station | SX 9996 8146 | 19 | #N/A | EXE ESTUARY | Exe | EXMOUTH BEACH | Commissioned pre-2016 - full year data expected | 27.44 | 18 | 100
South West Water | PHILLACK CSO | PHILLACK_CSO_HAYLE | 301821 | 301821/CS/01 | A1 | SO on sewer network | SW 5655 3821 | 136 | #N/A | HAYLE ESTUARY (E) |  | PORTH KIDNEY SANDS | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | VIADUCT HIGH LEVEL STORM TANK CSO | PIERMONT PL/JUBILEE BRIDGE_CSO_DAWLISH | 201449 | 201449 | A1 | SO on sewer network | SX 9630 7666 | GB108045008910 | Dawlish Water | DAWLISH WATER(C) |  | DAWLISH (TOWN) BEACH | Commissioned pre-2016 - full year data expected | 189.16 | 21 | 84 | Sensor failure / issue | Resolved - October
South West Water | PILLATON WASTEWATER TREATMEMT WORKS | PILLATON STW_SSO_PILLATON | NRA-SW-6741 | NRA-SW-6741 | A2 | Storm tank at WwTW | SX 3604 6400 | GB108047007670 | Lower River Lynher | RIVER LYNHER |  |  | Commissioned in 2019 - full year data expected | 1130.59 | 85 | 100
South West Water | PILTON QUAY CSO | PILTON QUAY_CSO_BARNSTAPLE | 203282 | 203282 | A1 | SO on sewer network | SS 5569 3377 | 198 | #N/A | TIDAL RIVER YEO(E) | Taw/Torridge |  | Commissioned pre-2016 - full year data expected | 3.38 | 9 | 100
South West Water | MALBOROUGH EJECTOR PS | PINHEY EJECTOR SPS_PSCSOEO_MALBOROUGH | 203408 | 203408 | A1 | Storm discharge at pumping station | SX 7109 4011 | 69 | #N/A | TRIB OF BLANKSMILL CREEK (S) | Salcombe |  | Commissioned pre-2016 - full year data expected | 286.98 | 49 | 100
South West Water | PITT HILL ROAD CSO | PITT HILL RD_CSO_NEWTON ABBOT | 203096 | 203096 | A1 | SO on sewer network | SX 8602 7219 | 22 | #N/A | S/W SEWER THEN TO WHITELAKE(S) | Teign |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | PIXON LANE COMBINED SEWER OVERFLOW | PIXON LN_CSO_TAVISTOCK | 300525/CS/01 | 300525 | A1 | SO on sewer network | SX 4791 7400 | GB108047007840 | Lower River Tavy | RIVER TAVY |  |  | Commissioned in 2019 - full year data expected | #N/A | #N/A | 0 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | PLAIDY PUMP STATION | PLAIDY SPS_PSCSO_LOOE | 300971 | 300971 | A1 | SO on sewer network | SX 2649 5384 | 265 | #N/A | LOOE BAY (C) |  | MILLENDREATH BEACH | Commissioned pre-2016 - full year data expected | 137.77 | 67 | 100
South West Water | PLAYING FIELD CSO | PLAYING FIELD_CSO_ERMINGTON | 201875 | 201875 | A1 | SO on sewer network | SX 6406 5308 | GB108046005200 | Erme | RIVER ERME |  | MOTHECOMBE BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 43 | Comms failure / issue | N/A - Ongoing investigation
South West Water | TAVISTOCK COLLEGE PLAYING FIELD | PLAYING FIELD_CSO_TAVISTOCK | 301678 | 301678 | A1 | SO on sewer network | SX 4765 7343 | GB108047007840 | Lower River Tavy | RIVER TAVY |  |  | Commissioned in 2017 - full year data expected | 193.23 | 53 | 66 | Comms failure / issue | Resolved - July | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
South West Water | PLAYING FIELDS PUMPING STATION | PLAYING FIELDS_PSCSOEO_CALSTOCK | 301614 | 301614 | A1 | Storm discharge at pumping station | SX 4363 6845 | 71 | #N/A | RIVER TAMAR (ESTUARINE) |  |  | Commissioned in 2017 - full year data expected | 394.19 | 75 | 100
South West Water | PLYMOUTH ROAD CSO | PLYMOUTH RD OPP DINGLE RD_CSO_PLYMPTON | 301763 | 301763 | A1 | SO on sewer network | SX 5326 5645 | GB108047003640 | Tory Brook | TORY BROOK |  | PLYMOUTH HOE (EAST) | Commissioned in 2016 - full year data expected | 72.99 | 70 | 100
South West Water | PLYMOUTH ROAD CSO | PLYMOUTH RD_CSO_TAVISTOCK | 301886 | 301886 | A1 | SO on sewer network | SX 4783 7396 | GB108047007840 | Lower River Tavy | RIVER TAVY VIA SWS |  |  | Commissioned in 2017 - full year data expected | 1.39 | 6 | 75 | Sensor failure / issue | Resolved - September
South West Water | OLD LAIRA ROAD JUNCTION CSO | PLYMOUTH ROAD/EMBANKMENT RD_CSO_PLYMOUTH | 301765 | 301765 | A1 | SO on sewer network | SX 5086 5588 | 73 | #N/A | RIVER PLYM (ESTUARINE) |  | PLYMOUTH HOE (EAST) | Commissioned in 2016 - full year data expected | 0.56 | 4 | 100
South West Water | PLYMTREE STW | PLYMTREE STW_SO_PLYMTREE | NRA-SW-3746 | NRA-SW-3746 | A2 | Inlet SO at WwTW | ST 0491 0279 | GB108045008860 | Upper Clyst | AN UNNAMED TRIB-RIVER CLYST |  |  | Commissioned in 2019 - full year data expected | 719.69 | 66 | 100
South West Water | POLGOOTH COMBINED SEWER OVERFLOW | POLGOOTH_CSO_ST AUSTELL | 303594 | 303594 | A1 | SO on sewer network | SX 0005 5018 | GB108048002280 | St Austell River | POLGOOTH STREAM |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 100
South West Water | LAPFORD PSCSO/EO | POLICE HOUSE SPS_PSCSOEO_LAPFORD | 202171 | 202171/PC/01 | A1 | Storm discharge at pumping station | SS 7269 0805 | GB108050014640 | Lower River Yeo (Lapford) | RIVER YEO (S) |  |  | EDM to be installed by December 2023
South West Water | POLKERRIS FINE SCREENING PLANT & PS | POLKERRIS SPST_PSCSOEO_POLKERRIS | 302706 | 302706 | A1 | Storm discharge at pumping station | SX 0912 5191 | 256 | #N/A | ST AUSTELL BAY (C) | St.Austell Bay |  | Commissioned in 2020 - full year data expected | 399.41 | 44 | 87 | Comms failure / issue | Resolved - April
South West Water | POLPERRO WWTW | POLPERRO FINESCREEN STW_CSO_POLPERRO | EPRCP3620XD | EPR/CP3620XD | A1 | SO on sewer network | SX 2128 5084 | 258 | #N/A | THE ENGLISH CHANNEL |  |  | Commissioned in 2019 - full year data expected | 90.6 | 47 | 100
South West Water | POLRUAN QUAY PS | POLRUAN QUAY SPS_PSCSOEO_POLRUAN | 302772 | 302772 | A1 | Storm discharge at pumping station | SX 1257 5107 | 26 | #N/A | RIVER FOWEY ESTUARY(E) | Fowey | READYMONEY COVE | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | POLSON HILL PSCSO/EO | POLSON HILL SPS_PSCSOEO_MORCHARD BISHOP | 201676 | 201676/PC/01 | A1 | Storm discharge at pumping station | SS 7698 0697 | GB108050008290 | Knighty Brook | STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | POLYPHANT PSCSO/EO | POLYPHANT SPST_PSCSOEO_POLYPHANT | 301646 | 301646/PC/01 | A1 | Storm discharge at pumping station | SX 2650 8220 | GB108047007760 | Upper River Inny | RIVER INNY (S) |  |  | EDM to be installed by December 2023
South West Water | PORT ISAAC PUMPING STATION | PORT ISAAC SPS_PSCSOEO_PORT ISAAC | 301630 | 301630 | A1 | Storm discharge at pumping station | SW 9946 8098 | 234 | #N/A | THE HAVEN, ATLANTIC OCEAN |  |  | Commissioned in 2020 - full year data expected | 0.58 | 2 | 100
South West Water | PORTHALLOW SEWAGE PUMPING STATION | PORTHALLOW SPST_PSCSOEO_HELFORD | 300969 | 300969/PC/01 | A1 | Storm discharge at pumping station | SW 7972 2318 | 404 | #N/A | PORTHALLOW STREAM (S) |  | PORTHALLOW BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | PORTHCURNO VALLEY PUMPING STATION | PORTHCURNO SPS_PSCSOEO_PENZANCE | 303618 | 303618 | A1 | Storm discharge at pumping station | SW 3873 2207 | 270 | #N/A | ATLANTIC OCEAN, OFF PORTHCURNO |  | PORTHCURNO BEACH | Commissioned pre-2016 - full year data expected | 383 | 22 | 99
South West Water | BAMALUZ POINT STORM WATER & EO | PORTHGWIDDEN SPST_PSCSOEO_ST IVES | NRA-SW-2266 | NRA-SW-2266 | A1 | Storm discharge at pumping station | SW 5228 4102 | 230 | #N/A | ST IVES BAY |  | PORTHGWIDDEN BEACH ST.IVES | Commissioned pre-2016 - full year data expected | 2.56 | 5 | 100
South West Water | PORTHILLY COVE PS | PORTHILLY SPST_PSCSOEO_PORTHILLY | 302972 | 302972 | A1 | Storm discharge at pumping station | SW 9373 7546 | 135 | #N/A | CAMEL ESTUARY (E) | Camel | ROCK BEACH | Commissioned pre-2016 - full year data expected | 3.85 | 9 | 100
South West Water | PORTHILLY COVE PS | PORTHILLY SPST_PSCSOEO_PORTHILLY | 302972 | 302972 | A1 | Storm discharge at pumping station | SW 9338 7524 | 135 | #N/A | CAMEL ESTUARY (E) | Camel | ROCK BEACH | Commissioned pre-2016 - full year data expected | 3.85 | 9 | 100
South West Water | PORTHMINSTER POINT 1 EO | PORTHMINSTER SPS_PSCSOEO_PORTHMINSTER | 2894/87 | 2894/87 | A1 | Storm discharge at pumping station | SW 5258 3957 | 230 | #N/A | ST IVES BAY ATLANTIC OCEAN |  | CARBIS BAY | Commissioned pre-2016 - full year data expected | 5.24 | 5 | 100
South West Water | PORTHPEAN PSCSO/EO | PORTHPEAN SPS_PSCSOEO_PORTHPEAN | 301670 | 301670/PC/01 | A1 | Storm discharge at pumping station | SX 0323 5051 | 256 | #N/A | ST AUSTELL BAY (C) |  | PORTHPEAN BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | ECHO CORNER PSCSO/EO | PORTHTOWAN No2 SPST_PSCSOEO_PORTHTOWAN | 302099 | 302099/PC/01 | A1 | Storm discharge at pumping station | SW 6953 4743 | 229 | #N/A | PORTHTOWAN STREAM (S) |  | PORTHTOWAN BEACH | Commissioned pre-2016 - full year data expected | 351.59 | 32 | 100
South West Water | PORTLOE WASTEWATER TREATMENT WORKS | PORTLOE FINESCN_SO_PORTLOE | 302776 | 302776 | A1 | Storm discharge at pumping station | SW 9380 3928 | 403 | #N/A | ENGLISH CHANNEL (COASTAL) |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 100
South West Water | PORTMARSH CSO | PORTMARSH FIELDS_CSO_BARNSTAPLE | 203283 | 203283 | A1 | SO on sewer network | SS 5640 3262 | GB108050019980 | Coney Gut | TRIB OF RIVER TAW ESTUARY (S) | Taw/Torridge |  | Commissioned pre-2016 - full year data expected | 0.69 | 2 | 100
South West Water | PORTMELLON PSCSO/EO | PORTMELLON SPS_PSCSOEO_MEVAGISSEY | 302115 | 302115/PC/01 | A1 | Storm discharge at pumping station | SX 0150 4389 | 256 | #N/A | STREAM (S) |  | PORTMELLON BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | PORTSCATHO SEWAGE TREATMENT WORKS | PORTSCATHO INLET SPS_PSCSOEO_PORTSCATHO | 302805 | 302805 | A1 | Storm discharge at pumping station | SW 8798 3515 | 403 | #N/A | PENCABE DRANG (COASTAL) |  |  | Commissioned in 2017 - full year data expected | 6.08 | 14 | 100
South West Water | PORTWRINKLE PSCSO/EO | PORTWRINKLE SPST_PSCSOEO_PORTWRINKLE | 302116 | 302116/PC/01 | A1 | Storm discharge at pumping station | SX 3620 5370 | 263 | #N/A | WHITSAND BAY (C) |  | PORTWRINKLE BEACH | Commissioned pre-2016 - full year data expected | 374.31 | 42 | 100
South West Water | PORTWRINKLE TANK CSO | PORTWRINKLE TANK_CSO_TORPOINT | 301864 | 301864/CS/01 | A1 | SO on sewer network | SX 3567 5371 | 263 | #N/A | WHITSAND BAY (C) |  | PORTWRINKLE BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | POTTERY QUAY PUMPING STATION | POTTERY QUAY SPS_PSCSOEO_PLYMOUTH | 301990 | 301990 | A1 | Storm discharge at pumping station | SX 4476 5530 | 73 | #N/A | PLYMOUTH SOUND (ESTUARINE) |  |  | Commissioned in 2016 - full year data expected | 95.45 | 36 | 100
South West Water | POTTINGTON PUMPING STATION | POTTINGTON EST SPS_PSCSOEO_BARNSTAPLE | 203284 | 203284 | A1 | Storm discharge at pumping station | SS 5484 3332 | 198 | #N/A | TAW ESTUARY & TRIBUTARY(E) | Taw/Torridge |  | Commissioned pre-2016 - full year data expected | 1628.49 | 88 | 100
South West Water | POUNDWELL MEADOW CSO | POUNDWELL MEADOW_CSO_MODBURY | 201962 | 201962 | A1 | SO on sewer network | SX 6573 5146 | GB108046005020 | Ayleston Brook | TRIBUTARY OF AYLESTON BROOK |  | MOTHECOMBE BEACH | Commissioned pre-2016 - full year data expected | 405.02 | 28 | 100
South West Water | PRINCE OF WALES PUMPING STATION | PR OF WALES PIER SPS_PSCSOEO_FALMOUTH | 303020 | 303020 | A1 | Storm discharge at pumping station | SW 8083 3302 | 402 | #N/A | THE PENRYN RIVER (E) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | #N/A | #N/A | 0 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | PRAZE TANK CSO | PRAZE TANK_CSO_PENRYN | 302302 | 302302 | A1 | SO on sewer network | SW 7810 3481 | 402 | #N/A | PRAZE STREAM | Fal Estuary |  | Commissioned in 2017 - full year data expected | 282.77 | 37 | 89 | Comms failure / issue | Resolved - December
South West Water | PRESTON GREEN ATTENUATION TANK | PRESTON GREEN SPS_PSCSOEO_PAIGNTON | 200239 | 200239 | A1 | Storm discharge at pumping station | SX 8987 6185 | 429 | #N/A | PRESTON SANDS (C) |  | PAIGNTON (PRESTON SANDS) | Commissioned pre-2016 - full year data expected | 10.05 | 11 | 100
South West Water | PRINCE OF WALES ROAD CSO | PRINCE OF WALES RD_CSO_KINGSBRIDGE | 203437 | 203437 | A1 | SO on sewer network | SX 7355 4401 | 69 | #N/A | KINGSBRIDGE ESTUARY(E) | Salcombe |  | Commissioned pre-2016 - full year data expected | 53.44 | 39 | 100
South West Water | PRIXFORD PUMPING STATION | PRIXFORD SPS_PSCSOEO_PRIXFORD | 201618 | 201618 | A1 | Storm discharge at pumping station | SS 5467 3665 | GB108050020020 | Knowl Water | TRIBUTARY OF KNOWLE WATER |  |  | Commissioned in 2019 - full year data expected | 553.91 | 37 | 100
South West Water | PROMENADE CSO- ILFRACOMBE RESEWERAG | PROMENADE_CSO_ILFRACOMBE | 004366/CS/01 | 004366/CS/01 | A1 | SO on sewer network | SS 5189 4782 | 237 | #N/A | WEST WILDER BROOK |  | ILFRACOMBE WILDERSMOUTH BEACH | Commissioned pre-2016 - full year data expected | 0.14 | 1 | 100
South West Water | PUDDINGTON STW | PUDDINGTON STW_SO_PUDDINGTON | SWWA 981 | SWWA 981 | A2 | Inlet SO at WwTW | SS 8360 1073 | GB108045014910 | Upper Creedy | RIVER CREEDY |  |  | EDM to be installed by December 2023
South West Water | DERRIL SPS | PYWORTHY SPST_PSCSOEO_DERRIL | 301649 | 301649/PC/01 | A1 | Storm discharge at pumping station | SS 3074 0375 | GB108047008070 | Derril Water | RIVER DERRIL (S) |  |  | EDM to be installed by December 2023
South West Water | QUARRY CLOSE CSO | QUARRY CLOSE_CSO_TOTNES | 202965 | 202965 | A1 | SO on sewer network | SX 7904 6054 | 23 | #N/A | TRIBUTARY OF MALT MILL LAKE | Dart |  | Commissioned in 2018 - full year data expected | 40.72 | 19 | 46 | Comms failure / issue | Resolved - January
South West Water | QUAY HILL CSO | QUAY HILL R/O CUSTOM HSE_CSO_EXETER | 201899 | 201899 | A1 | SO on sewer network | SX 9194 9215 | GB108045009040 | Exe (Creedy to Estuary) | HIGHER LEAT VIA SW SEWER | Exe |  | Commissioned in 2019 - full year data expected | 1.03 | 4 | 100
South West Water | QUAY HILL COMBINED SEWER OVERFLOW | QUAY HILL_CSO_EXETER | 201901 | 201901 | A1 | SO on sewer network | SX 9192 9217 | GB108045009040 | Exe (Creedy to Estuary) | HIGHER LEAT | Exe |  | Commissioned in 2017 - full year data expected | 0.21 | 2 | 100
South West Water | QUEEN MARY GARDENS PUMPING STATION | QUEEN MARY GARDENS SPS_PSCSOEO_FALMOUTH | 300227 | 300227/PC/01 | A1 | Storm discharge at pumping station | SW 8074 3131 | 402 | #N/A | FALMOUTH BAY (E) |  | SWANPOOL BEACH | Commissioned pre-2016 - full year data expected | 27.28 | 40 | 100
South West Water | QUEEN STREET CSO | QUEEN ST/COURTNEY ST_CSO_NEWTON ABBOT | 203573 | 203573 | A1 | SO on sewer network | SX 8603 7138 | GB108046008450 | Lemon | RIVER LEMON VIA SWS(S) | Teign |  | Commissioned pre-2016 - full year data expected | 0.74 | 3 | 100
South West Water | QUEENSWAY PUMPING STATION | QUEENSWAY SPS_PSCSOEO_NEWTON ABBOT | 203103 | 203103 | A1 | Storm discharge at pumping station | SX 8719 7071 | GB108046005350 | Aller Brook (Teign) - Lower | SWS TO THE ALLER BROOK (S) | Teign |  | Commissioned pre-2016 - full year data expected | 57.06 | 13 | 100
South West Water | QUENCHWELL PUMPING STATION | QUENCHWELL SPS_PSCSOEO_CARNON DOWNS | 302992 | 302992 | A1 | Storm discharge at pumping station | SW 7968 4083 | GB108048001231 | Lower River Carnon | TRIB OF CARNON RIVER | Fal Estuary |  | Commissioned in 2016 - full year data expected | 167.6 | 39 | 100
South West Water | QUETHIOCK WWTW | QUETHIOCK STW_SO_QUETHIOCK | SWWA 1148 | SWWA 1148 | A2 | Inlet SO at WwTW | SX 3129 6461 | GB108047003890 | Tiddy | TRIBUTARY OF THE RIVER TIDDY |  |  | Commissioned in 2018 - full year data expected | 901.98 | 310 | 100
South West Water | BITTON PARK RUGBY CLUB CSO | R/O 137 BITTON PARK ROAD_CSO_TEIGNMOUTH | 203346 | 203346 | A1 | SO on sewer network | SX 9328 7296 | 22 | #N/A | TEIGN ESTUARY (E) | Teign |  | Commissioned in 2016 - full year data expected | 6.23 | 4 | 100
South West Water | 19 HEAVITREE ROAD CSO | R/O 19 HEAVITREE RD_CSO_EXETER | 201921 | 201921 | A1 | SO on sewer network | SX 9223 9188 | GB108045009040 | Exe (Creedy to Estuary) | RIVER EXE VIA SWS | Exe |  | Commissioned in 2018 - full year data expected | 10.2 | 19 | 100
South West Water | R/O 615 WOLSELEY ROAD | R/O 615 WOLSELEY ROAD_CSO_PLYMOUTH | 302617 | 302617 | A1 | SO on sewer network | SX 4459 5801 | 73 | #N/A | KINTERBURY CREEK VIA W/CRSE(S) | Tamar |  | Commissioned pre-2016 - full year data expected | 0.21 | 1 | 100
South West Water | DENHAM CLOSE CSO | R/O 9 DENHAM CLOSE_CSO_PLYMOUTH | 301724 | 301724 | A1 | SO on sewer network | SX 4734 5880 | 73 | #N/A | HONICKNOWLE STREAM |  |  | Commissioned in 2016 - full year data expected | 0.98 | 6 | 100
South West Water | ORCHARD CLOSE CSO | R/O ORCHARD CLOSE_CSO_SHALDON | 203085 | 203085 | A1 | SO on sewer network | SX 9256 7204 | 22 | #N/A | RINGMORE STREAM (S) | Teign |  | Commissioned pre-2016 - full year data expected | 4.12 | 19 | 100
South West Water | HONICKNOWLE CSO | R/O QUARRY COTTAGES_CSO_HONICKNOWLE LN | 303435 | 303435 | A1 | SO on sewer network | SX 4679 5865 | 73 | #N/A | HONICKNOWLE STREAM (S) | Tamar |  | Commissioned pre-2016 - full year data expected | 44.32 | 24 | 100
South West Water | RACKENFORD WWTW SSO | RACKENFORD STW_SO_RACKENFORD | NRA-SW-1492 | NRA-SW-1492 | A2 | Inlet SO at WwTW | SS 8506 1783 | GB108050013980 | Upper Little Dart River | TRIB. OF LITTLE DART RIVER |  |  | EDM to be installed by December 2023
South West Water | RADFORD STW | RADFORD STW_SO_PLYMOUTH | 301935 | 301935 | A2 | Inlet SO at WwTW | SX 5019 5283 | 73 | #N/A | HOOE LAKE |  | PLYMOUTH HOE (EAST) | Commissioned pre-2016 - full year data expected | 160.23 | 71 | 100
South West Water | RADFORD STW | RADFORD STW_SSO_PLYMOUTH | 301935 | 301935 | A3 | Storm tank at WwTW | SX 5019 5283 | 73 | #N/A | HOOE LAKE |  | PLYMOUTH HOE (EAST) | Commissioned pre-2016 - full year data expected | 122.86 | 14 | 100
South West Water | RAILWAY PSCSO/EO | RAILWAY SPS_PSCSOEO_LAPFORD | 202173 | 202173/PC/01 | A1 | Storm discharge at pumping station | SS 7291 0750 | GB108050014640 | Lower River Yeo (Lapford) | TRIB OF RIVER YEO (S) |  |  | EDM to be installed by December 2023
South West Water | STATION CAR PARK CSO | RAILWAY STATION CAR PARK_CSO_TEIGNMOUTH | 203349 | 203349 | A1 | SO on sewer network | SX 9456 7320 | 410 | #N/A | LYME BAY (VIA SURF WTR SEWER) |  | TEIGNMOUTH (TOWN) BEACH | Commissioned pre-2016 - full year data expected | 13.77 | 7 | 54 | Comms failure / issue | Resolved - September
South West Water | RALEIGH HILL CSO | RALEIGH HILL_CSO_BIDEFORD | 203120 | 203120 | A1 | SO on sewer network | SS 4485 2763 | GB108050014500 | Kenwith Stream | KENWITH STREAM (S) | Taw/Torridge |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | PIKE ROAD COMBINED SEWER OVERFLOW | RD OUTSIDE 31A PIKE RD_CSO_PLYMOUTH | 301708 | 301708 | A1 | SO on sewer network | SX 5086 5588 | 73 | #N/A | RIVER PLYM VIA SWS (ESTUARINE) |  | PLYMOUTH HOE (EAST & WEST) | Commissioned in 2016 - full year data expected | 201.68 | 102 | 100
South West Water | READYMONEY COVE PS | READY MONEY COVE SPS_PSCSOEO_FOWEY | 302771 | 302771 | A1 | Storm discharge at pumping station | SX 1188 5100 | 26 | #N/A | RIVER FOWEY ESTUARY(E) | Fowey | READYMONEY COVE | Commissioned pre-2016 - full year data expected | 2.33 | 2 | 100
South West Water | READYMONEY ROAD COMBINED SEWER | READYMONEY ROAD_CSO_FOWEY | 302770 | 302770 | A1 | SO on sewer network | SX 1200 5111 | 26 | #N/A | RIVER FOWEY ESTUARY(E) | Fowey | READYMONEY COVE | Commissioned pre-2016 - full year data expected | 8.19 | 10 | 88 | Comms failure / issue | Resolved - May
South West Water | R/O IMPERIAL HOTEL CSO | REAR IMPERIAL HOTEL_CSO_EXETER | 201902 | 201902 | A1 | SO on sewer network | SX 9141 9349 | GB108045009040 | Exe (Creedy to Estuary) | TADDIFORDE BROOK | Exe |  | Commissioned in 2018 - full year data expected | 6.43 | 14 | 100
South West Water | RECREATION GROUND CSO | REC GROUND_CSO_NEWTON POPPLEFORD | 201843 | 201843/CS/01 | A1 | SO on sewer network | SY 0873 8987 | GB108045009170 | Lower River Otter | BACK BROOK |  |  | Commissioned in 2019 - full year data expected | 40.13 | 10 | 100
South West Water | RELISTIAN PUMPING STATION | RELISTIAN SPS_PSCSOEO_RELISTIAN | 301607 | 301607 | A1 | Storm discharge at pumping station | SW 6039 3662 | GB108049000520 | Angarrack Stream | TRIB OF ANGARRACK STREAN |  |  | Commissioned in 2019 - full year data expected | 86.52 | 36 | 100
South West Water | RESCORLA CSO | RESCORLA_CSO_LUXULYAN | 301681 | 301681/CS/01 | A1 | SO on sewer network | SX 0332 5788 | GB108048002310 | Par River (Upper) | TRIB OF PAR SANDS (S) |  |  | EDM to be installed by December 2023
South West Water | RESKADINNICK PUMPING STATION | RESKADINNICK SPST_PSCSOEO_CAMBORNE | 301916 | 301916/PC/01 | A1 | Storm discharge at pumping station | SW 6341 4203 | GB108049000600 | Red River (Upper) | RED RIVER (S) |  | GWITHIAN TOWANS & GODREVY | Commissioned pre-2016 - full year data expected | 77.46 | 26 | 100
South West Water | REWE WASTEWATER TREATMENT WORKS | REWE STW_SSO_REWE | DRA 308 | DRA 308 | A2 | Storm tank at WwTW | SX 9455 9884 | GB108045014970 | Lower Culm | RIVER CULM |  |  | Commissioned in 2019 - full year data expected | 1632.58 | 100 | 100
South West Water | RIDDLECOMBE WASTE WATER TREATMENT | RIDDLECOMBE S T STW_SO_RIDDLECOMBE | 200417 | 200417 | A2 | Inlet SO at WwTW | SS 6084 1380 | GB108050014310 | Mully Brook | TRIBUTARY OF MULLY BROOK(S) |  |  | EDM to be installed by December 2023
South West Water | RILLA MILL WWTW | RILLA MILL STW_SO_RILLA MILL | NRA-SW-6622 | NRA-SW-6622 | A2 | Inlet SO at WwTW | SX 2941 7337 | GB108047007670 | Lower River Lynher | (S) RIVER LYNHER |  |  | Commissioned in 2018 - full year data expected | 3166.57 | 355 | 100
South West Water | RINGMORE ROAD CSO | RINGMORE RD_CSO_SHALDON | 203086 | 203086 | A1 | SO on sewer network | SX 9264 7236 | 22 | #N/A | TEIGN ESTUARY (E) | Teign |  | Commissioned pre-2016 - full year data expected | 21.63 | 25 | 100
South West Water | RINGMORE STW | RINGMORE STW_SSO_RINGMORE | 203013 | 203013 | A2 | Storm tank at WwTW | SX 6465 4578 | 266 | N/A | RINGMORE STREAM(S) |  |  | EDM to be installed by December 2023
South West Water | RIVER SIDE NO 1 CSO | RIVERSIDE NO. 1_CSO_NEWTON FERRERS | 301862 | 301862 | A1 | SO on sewer network | SX 5485 4788 | 70 | #N/A | NEWTON CREEK (ESTUARINE) | Yealm |  | Commissioned in 2017 - full year data expected | 8.73 | 9 | 100
South West Water | RIVERSIDE CSO | RIVERSIDE_CSO_BOVEY TRACEY | 201804 | 201804 | A1 | SO on sewer network | SX 8163 7819 | GB108046008470 | Lower Bovey | RIVER BOVEY VIA SW SEWER | Teign |  | Commissioned in 2017 - full year data expected | 0 | 0 | 100
South West Water | KINTERBURY CREEK RIVERSIDE PS | RIVERSIDE_PSCSOEO_PLYMOUTH | NRA-SW-6015 | NRA-SW-6015 | A1 | Storm discharge at pumping station | SX 4367 5845 | 73 | #N/A | RIVER TAMAR (ESTUARINE) |  | PLYMOUTH HOE (EAST) | Commissioned in 2016 - full year data expected | 2.98 | 2 | 100
South West Water | RIVERVIEW PSCSO/EO | RIVERVIEW No2 SPS_PSCSOEO_SALTASH | 302592 | 302592 | A1 | Storm discharge at pumping station | SX 4299 5947 | 71 | #N/A | SALTMILL CREEK(E) | Tamar |  | Commissioned pre-2016 - full year data expected | 87.02 | 14 | 100
South West Water | RIVERVIEW CSO | RIVERVIEW_CSO_SALTASH | 302588 | 302588 | A1 | SO on sewer network | SX 4306 5946 | 71 | #N/A | SALTMILL CREEK(E) | Tamar |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | ROBERTS OPE CSO | ROBERTS OPE_CSO_TRURO | 302669 | 302669 | A1 | SO on sewer network | SW 8261 4475 | GB108048002340 | Kenwyn | RIVER KENWYN[S] | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 611.53 | 185 | 100
South West Water | ROBOROUGH STW | ROBOROUGH STW_SSO_ROBOROUGH | NRA-SW-1504 | NRA-SW-1504 | A2 | Storm tank at WwTW | SS 5750 1676 | GB108050014320 | Woolleigh Brook | TRIB. OF WOOLLEIGH BROOK |  |  | EDM to be installed by December 2023
South West Water | ROCHE COMBINED SEWER OVERFLOW | ROCHE_CSO_ROCHE | 301682 | 301682 | A1 | SO on sewer network | SW 9929 6034 | GB108048002310 | Par River (Upper) | PAR RIVER |  |  | Commissioned in 2020 - full year data expected | 13.12 | 26 | 60 | Comms failure / issue | Resolved - November
South West Water | LYNTON/LYNMOUTH SEWERAGE | ROCK HOUSE SPS_PSCSOEO_LYNMOUTH | 004515/PC/01 | 004515/PC/01 | A1 | Storm discharge at pumping station | SS 7229 4962 | 237 | #N/A | LYNMOUTH BAY (E) |  | LYNMOUTH BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | ROCK PARK CSO | ROCK PARK SPS_PSCSOEO_BARNSTAPLE | 203285 | 203285 | A1 | Storm discharge at pumping station | SS 5615 3252 | GB108050019980 | Coney Gut | TAW ESTUARY(E) & CONEY GUT(S) | Taw/Torridge |  | Commissioned pre-2016 - full year data expected | 9.21 | 26 | 100
South West Water | ROCK PUMPING STATION | ROCK SPS_PSCSOEO_ST MINVER | 302971 | 302971 | A1 | Storm discharge at pumping station | SW 9307 7560 | 135 | #N/A | CAMEL ESTUARY (E) | Camel | ROCK BEACH | Commissioned pre-2016 - full year data expected | 1.63 | 2 | 100
South West Water | ROLLE ROAD COMBINED SEWER OVERFLOW | ROLLE RD_CSO_TORRINGTON | 200076/CS/01 | 200076 | A1 | SO on sewer network | SS 4990 1871 | GB108050014660 | Torridge (Lew to Estuary) | CASTLE HILL STREAM | Taw/Torridge |  | Commissioned in 2018 - full year data expected | 138.46 | 86 | 81 | Sensor failure / issue | Resolved - December
South West Water | ROSE COTTAGE CSO | ROSE COTTAGE_CSO_TEDBURN ST. MARY | 201705 | 201705/CS/01 | A1 | SO on sewer network | SX 8228 9412 | GB108045009220 | Culvery River | LILLY BROOK (S) |  |  | EDM to be installed by December 2023
South West Water | ROWING CLUB NO1 CSO | ROWING CLUB NO1_CSO_TORPOINT | 301641 | 301641 | A1 | SO on sewer network | SX 4418 5499 | 72 | #N/A | RIVER TAMAR (ESTUARINE) |  |  | Commissioned in 2017 - full year data expected | 2.87 | 7 | 100
South West Water | ROWING CLUB NO2 CSO | ROWING CLUB NO2_CSO_TORPOINT | 301642 | 301642 | A1 | SO on sewer network | SX 4418 5499 | 72 | #N/A | RIVER TAMAR (ESTUARINE) |  |  | Commissioned in 2017 - full year data expected | 52.18 | 47 | 100
South West Water | RUZZA PUMPING STATION | RUZZA SPS_PSCSOEO_NEWQUAY | 15/49/26/P/66 | 15/49/26/P/66 | A1 | Storm discharge at pumping station | SW 7832 5915 | 229 | #N/A | TRIB OF PORTH JOKE |  |  | Commissioned in 2016 - full year data expected | 0 | 1 | 100
South West Water | 1 EDNA TERRACE CSO | S/O ENTRY 1 EDNA TERRACE_CSO_PLYMOUTH | 301737 | 301737 | A1 | SO on sewer network | SX 5015 5478 | 73 | #N/A | RIVER PLYM VIA SWS (ESTUARINE) |  | PLYMOUTH HOE (EAST) | Commissioned in 2017 - full year data expected | 11.61 | 16 | 100
South West Water | SALTASH ROAD SPS PLYMOUTH | SALTASH ROAD SPS_PSCSOEO_PLYMOUTH | 301983 | 301983 | A1 | Storm discharge at pumping station | SX 4456 5590 | 73 | #N/A | RIVER TAMAR (ESTUARINE) |  |  | Commissioned in 2016 - full year data expected | 7.22 | 11 | 100
South West Water | SALTASH ROAD SPS PLYMOUTH | SALTASH ROAD SPS_PSCSOEO_PLYMOUTH | 301983 | 301983 | A1 | Storm discharge at pumping station | SX 4483 5605 | 73 | #N/A | RIVER TAMAR (ESTUARINE) |  |  | Commissioned in 2016 - full year data expected | 7.22 | 11 | 100
South West Water | SAMPFORD PEVERELL WWTW | SAMPFORD PEVERELL STW_SSO_SAMPFORD P | DRA 20 | DRA 20 | A2 | Storm tank at WwTW | ST 0387 1336 | GB108045015020 | Spratford Stream | SPRATFORD STREAM |  |  | Commissioned in 2018 - full year data expected | 664.75 | 81 | 100
South West Water | SANDFORD WASTEWATER TREATMENT WORKS | SANDFORD STW_SO_SANDFORD | DRA 262 | DRA 262 | A2 | Inlet SO at WwTW | SS 8339 0224 | GB108045009090 | Middle Creedy | TRIBUTARY OF RIVER CREEDY |  |  | Commissioned in 2020 - full year data expected | 59.42 | 40 | 100
South West Water | SANDY LANE PUMPING STATION | SANDY LANE LF SPST_PSCSOEO_DAWLISH | 201966 | 201966 | A1 | Storm discharge at pumping station | SX 9736 7649 | 20 | #N/A | LYME BAY (COASTAL) |  |  | Commissioned pre-2016 - full year data expected | 66.61 | 44 | 100
South West Water | SANDY LANE PUMPING STATION | SANDY LANE SPST_PSCSOEO_DAWLISH | 200898 | 200898/PC/01 | A1 | Storm discharge at pumping station | SX 9742 7647 | 20 | #N/A | LYME BAY (C) |  | DAWLISH (TOWN) BEACH | Commissioned in 2016 - full year data expected | 198.48 | 32 | 100
South West Water | SAUNTON ROAD PUMPING STATION | SAUNTON RD SPS_PSCSOEO_BRAUNTON | 200214/PC/01 | 200214 | A1 | Storm discharge at pumping station | SS 4739 3690 | GB108050020000 | Taw Estuary | TRIBUTARY OF SIR ARTHUR'S PILL |  |  | Commissioned in 2017 - full year data expected | 90.61 | 32 | 100
South West Water | SAWMILL SSO | SAW MILLS_CSO_MORETONHAMPSTEAD | NRA-SW-5468 | NRA-SW-5468 | A1 | SO on sewer network | SX 7592 8588 | GB108046008330 | Wray Brook | THE WRAY BROOK |  |  | EDM to be installed by December 2023
South West Water | SCARNE INDUSTRIAL ESTATE PSCSO/EO | SCARNE IND ESTATE SPS_PSCSOEO_LAUNCESTON | 301624 | 301624/PC/01 | A1 | Storm discharge at pumping station | SX 3403 8333 | GB108047007920 | Lowley Brook | LOWLEY BROOK (S) |  |  | EDM to be installed by December 2023
South West Water | SCAWNS HILL CSO | SCAWNS HILL_CSO_MENHENIOT | 301857 | 301857 | A1 | SO on sewer network | SX 2846 6298 | GB108048002320 | Seaton | TRIBUTARY OF THE RIVER SEATON |  | SEATON BEACH (CORNWALL) | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | SCOTTS BRIDGE PUMPING STATION | SCOTTS BRIDGE SPS_PSCSOEO_TORQUAY2 | 201624 | 201624 | A1 | Storm discharge at pumping station | SX 8918 6623 | GB108046005330 | Aller Brook (Teign) - Upper | ALLER BROOK |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 84 | Sensor failure / issue | Resolved - August
South West Water | SCOUT HUT CSO | SCOUT HUT_CSO_STOKE GABRIEL | 202853 | 202853 | A1 | SO on sewer network | SX 8502 5714 | 23 | #N/A | RIVER DART ESTUARY(E) | Dart |  | Commissioned pre-2016 - full year data expected | 242.12 | 28 | 89 | Comms failure / issue | Resolved - May
South West Water | MEMORIAL GARDENS PS | SEA HILL SPS_PSCSOEO_BEER | 202679 | 202679 | A1 | Storm discharge at pumping station | SY 2268 8783 | 407 | #N/A | LYME BAY AND SEATON BAY (C) |  | BEER BEACH | Commissioned pre-2016 - full year data expected | 21.59 | 28 | 98
South West Water | SEA LAWNS OUTFALL CSO, DAWLISH | SEA LAWN OUTFALL_CSO_DAWLISH | 200828 | 200828 | A1 | SO on sewer network | SX 9678 7705 | 20 | #N/A | LYME BAY(C) |  | DAWLISH (TOWN) BEACH | Commissioned pre-2016 - full year data expected | 3.76 | 4 | 100
South West Water | SEA LAWNS PUMPING STATION | SEA LAWNS SPS_PSCSOEO_DAWLISH | 200827 | 200827 | A1 | Storm discharge at pumping station | SX 9679 7705 | 20 | #N/A | LYME BAY |  |  | Commissioned pre-2016 - full year data expected | 10.63 | 16 | 100
South West Water | SEATON STW | SEATON SOUTH STW_SSO_EAST DEVON | 202563 | 202563 | A2 | Storm tank at WwTW | SY 2529 9081 | 17 | #N/A | RIVER AXE ESTUARY(E) |  | SEATON BEACH | Commissioned pre-2016 - full year data expected | 882.44 | 61 | 100
South West Water | SEATON PUMPING STATION | SEATON SPS_PSCSOEO_SEATON | 037806/PC/01 | 037806/PC/01 | A1 | Storm discharge at pumping station | SX 3016 5418 | 265 | #N/A | ENGLISH CHANNEL |  | SEATON BEACH (CORNWALL) | Commissioned pre-2016 - full year data expected | 1055 | 84 | 100
South West Water | SENNEN COVE PUMPING STATION | SENNEN SPS_PSCSOEO_LANDS END | 303620 | 303620 | A1 | Storm discharge at pumping station | SW 3495 2642 | 230 | #N/A | ATLANTIC OCEAN,OFF SENNEN COVE |  | SENNEN BEACH | Commissioned pre-2016 - full year data expected | 184.98 | 20 | 100
South West Water | SEYMOUR AVENUE/BEAUMONT RD CSO | SEYMOUR AVENUE/BEAUMONT ROAD_PLYMOUTH | 301735 | 301735 | A2 | SO on sewer network | SX 5015 5478 | 73 | #N/A | RIVER PLYM VIA SWS (ESTUARINE) |  | PLYMOUTH HOE (EAST & WEST) | Commissioned in 2017 - full year data expected | 2.69 | 11 | 100
South West Water | SEYMOUR AVENUE/SALISBURY RD CSO | SEYMOUR AVENUE/SALISBURY RD_CSO_PLYMOUTH | 301734 | 301734 | A1 | SO on sewer network | SX 5015 5478 | 73 | #N/A | RIVER PLYM VIA SWS (ESTUARINE) |  | PLYMOUTH HOE (EAST) | Commissioned in 2017 - full year data expected | 8.34 | 23 | 100
South West Water | SEYMOUR PLACE CSO | SEYMOUR PLACE_CSO_PLYMOUTH | 301749 | 301749/CS/01 | A1 | SO on sewer network | SX 4622 5441 | 73 | #N/A | STONEHOUSE CREEK (E) |  |  | EDM to be installed by December 2023
South West Water | STOKE FLEMING PUMPING STATION | SHADY LANE SPS_PSCSOEO_STOKE FLEMING | 203363 | 203363 | A1 | Storm discharge at pumping station | SX 8638 4835 | 260 | #N/A | LEONARDS COVE STREAM |  |  | Commissioned in 2016 - full year data expected | 399.51 | 51 | 100
South West Water | SHADYCOMBE LOWER TUNNEL | SHADYCOMBE TANK_CSOEO_SALCOMBE | 003224/PC/01 | 003224/PC/01 | A1 | SO on sewer network | SX 7417 3934 | 69 | #N/A | SHADYCOMBE CREEK |  | MILL BAY BEACH | Commissioned pre-2016 - full year data expected | 9.06 | 9 | 100
South West Water | SHADYCOMBE LOWER TUNNEL | SHADYCOMBE TK LOWER TUNNELS_CSO_SALCOMBE | 200070/PC/01 | 200070 | A1 | SO on sewer network | SX 7417 3934 | 69 | #N/A | BATSON CREEK (ESTUARINE) |  |  | Commissioned pre-2016 - full year data expected | 17.22 | 8 | 100
South West Water | KING GEORGE'S FIELD PS | SHALDON SPST_PSCSOEO_TEIGNMOUTH | 203348 | 203348 | A1 | Storm discharge at pumping station | SX 9301 7246 | 22 | #N/A | TEIGN ESTUARY(E) | Teign | SHALDON BEACH | Commissioned pre-2016 - full year data expected | 27.49 | 12 | 100
South West Water | SHAND PARK CSO | SHAND PARK_CSO_AXMINSTER | 203642 | 203642 | A1 | SO on sewer network | SY 2938 9843 | GB108045008870 | Lower Axe | TRIB OF THE RIVER AXE |  |  | Commissioned in 2019 - full year data expected | 30 | 15 | 100
South West Water | SHEBBEAR WASTEWATER TREATMENT WORKS | SHEBBEAR STW_SO_SHEBBEAR | NRA-SW-3849 | NRA-SW-3849 | A2 | Inlet SO at WwTW | SS 4250 0910 | GB108050013930 | Torridge (Combe Lake to Lew) | RIVER TORRIDGE |  |  | Commissioned in 2019 - full year data expected | 1510.35 | 135 | 100
South West Water | SHEEPWASH WWTW | SHEEPWASH STW_SO_SHEEPWASH | SWWA 496 | SWWA 496 | A2 | Inlet SO at WwTW | SS 4847 0595 | GB108050013930 | Torridge (Combe Lake to Lew) | RIVER TORRIDGE |  |  | Commissioned in 2019 - full year data expected | 594.2 | 58 | 55 | Comms failure / issue | Resolved - October
South West Water | SHERFORD WASTEWATER TREATMENT WORKS | SHERFORD STW_SO_SHERFORD | NRA-SW-6171 | NRA-SW-6171 | A2 | Inlet SO at WwTW | SX 7784 4429 | GB108046004760 | Avon (DevonTidal) and Sth Hams - Frogmore | SHERFORD STREAM | Salcombe |  | Commissioned in 2019 - full year data expected | 2003.27 | 226 | 100
South West Water | SHEVIOCK STW SO | SHEVIOCK S T SEPTNK_SO_SHEVIOCK | NRA-SW-1518 | NRA-SW-1518 | A2 | Inlet SO at WwTW | SX 3740 5490 | 72 | #N/A | RIVER LYNHER | Lynher |  | Commissioned in 2019 - full year data expected | 293.69 | 17 | 98
South West Water | SHIELING ROAD CSO | SHIELING RD_CSO_BICKINGTON | 203289 | 203289 | A1 | SO on sewer network | SS 5290 3239 | 198 | #N/A | BRYN BROOK(S) | Taw/Torridge |  | Commissioned pre-2016 - full year data expected | 0.14 | 1 | 99
South West Water | SHILLINGFORD ST GEORGE WWTW CSO | SHILLINGFORD ST GEORGE STW_SO_SHILLINGFD | NRA-SW-1521 | NRA-SW-1521 | A2 | Inlet SO at WwTW | SX 9073 8798 | GB108045009000 | Matford Brook | ALPHIN BROOK |  |  | EDM to be installed by December 2023
South West Water | SHINNER'S BRIDGE CSO | SHINNERS BRIDGE_CSO_DARTINGTON | 202966 | 202966 | A1 | SO on sewer network | SX 7879 6215 | GB108046005160 | Bidwell Brook | BIDWELL BROOK | Dart |  | Commissioned in 2019 - full year data expected | 36.42 | 31 | 74 | Comms failure / issue | Resolved - November
South West Water | SHIP INN CSO | SHIP INN_CSO_COCKWOOD | 202630 | 202630 | A1 | SO on sewer network | SX 9752 8069 | 20 | #N/A | COFTON STREAM(S) | Exe |  | Commissioned pre-2016 - full year data expected | 2.06 | 10 | 100
South West Water | SHIPWRIGHTS PUMPING STATION | SHIPWRIGHTS SPS_PSCSOEO_HELFORD | 303454 | 303454 | A1 | Storm discharge at pumping station | SW 7584 2620 | 75 | #N/A | THE HELFORD CREEK(E) | Helford |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 53 | Comms failure / issue | Resolved - January
South West Water | SHIRLEY GARDENS CSO | SHIRLEY GARDENS_CSO_PLYMOUTH | 301723 | 301723 | A1 | SO on sewer network | SX 4725 5805 | 73 | #N/A | HAM BROOK |  | PLYMOUTH HOE (EAST) | Commissioned in 2017 - full year data expected | 0.19 | 1 | 86 | Sensor failure / issue | Resolved - February
South West Water | QUILLETTS CSO | SHUTE PARK_CSO_MALBOROUGH | NRA-SW-7653/CS/1 | NRA-SW-7653 | A1 | SO on sewer network | SX 7079 3949 | 430 | #N/A | TRIBUTARY OF COMBE STREAM |  | SALCOMBE SOUTH SANDS | Commissioned pre-2016 - full year data expected | 38.02 | 49 | 100
South West Water | SHUTE WWTW | SHUTE_SO_EXETER | 203276 | 203276 | A2 | Inlet SO at WwTW | SS 8954 0008 | GB108045009080 | Jackmoor Brook | TRIB OF RIVER CREEDY |  |  | EDM to be installed by December 2023
South West Water | SHUTTERTON BRIDGE PS | SHUTTERTON BRIDGE SPS_PSCSO_DAWLISH | 202632 | 202632 | A1 | SO on sewer network | SX 9657 7854 | 20 | #N/A | SHUTTERTON BROOK(S) | Exe |  | Commissioned pre-2016 - full year data expected | 0.6 | 2 | 100
South West Water | BROADCLYST (SIDE) PUMPING STATION | SIDE SPS_PSCSOEO_BROADCLYST | 201639 | 201639 | A1 | Storm discharge at pumping station | SX 9851 9740 | GB108045008860 | Upper Clyst | RIVER CLYST VALLEY VIA SWS | Exe |  | Commissioned in 2016 - full year data expected | 17.52 | 14 | 100
South West Water | SILVERTON PUMPING STATION | SILVERTON SPS_PSCSOEO_SILVERTON | 203704 | 203704 | A1 | Storm discharge at pumping station | SS 9527 0301 | GB108045015050 | Exe (Barle to Culm) | SILVERTON STREAM VIA SWS |  |  | Commissioned in 2019 - full year data expected | 8.09 | 11 | 100
South West Water | SILVERTON WWTW | SILVERTON STW_SSO_SILVERTON | SWWA 5 | SWWA 5 | A2 | Storm tank at WwTW | SS 9712 0142 | GB108045014970 | Lower Culm | HEAL-EYE STREAM |  |  | Commissioned in 2019 - full year data expected | 692.64 | 42 | 100
South West Water | SKERN CSO | SKERN_CSO_APPLEDORE | 002884/CS/01 | 002884/CS/01 | A1 | SO on sewer network | SS 4528 3038 | 199 | #N/A | THE PILL | Taw/Torridge | INSTOW BEACH | Commissioned pre-2016 - full year data expected | 25.79 | 41 | 96
South West Water | SLAPTON WASTEWATER TREATMENT WORKS | SLAPTON STW_SSO_SLAPTON | 203034 | 203034 | A2 | Storm tank at WwTW | SX 8205 4438 | GB108046004810 | Avon (Devon Tidal) and Sth Hams - Slapton | START BAY/SLAPTON LEY |  |  | Commissioned pre-2016 - full year data expected | 298.54 | 46 | 100
South West Water | KIMBERLEY NURSERIES CSO | SLAPTON_CSO_SLAPTON | 201721 | 201721/CS/01 | A1 | SO on sewer network | SX 8214 4478 | GB108046004810 | Avon (Devon Tidal) and Sth Hams - Slapton | STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | SLITTERCOMBE LANE PSCSO/EO | SLITTERCOMBE SPST_PSCSOEO_KENTON | 202626 | 202626 | A1 | Storm discharge at pumping station | SX 9613 8347 | 20 | #N/A | RIVER KENN(S) | Exe |  | Commissioned pre-2016 - full year data expected | 16.84 | 8 | 100
South West Water | SMITH STREET CSO | SMITH ST_CSO_DARTMOUTH | 202400 | 202400 | A1 | SO on sewer network | SX 8793 5124 | 23 | #N/A | RIVER DART VIA SWS (ESTUARINE) |  |  | Commissioned in 2019 - full year data expected | 174.91 | 100 | 100
South West Water | CSO AT SMITHICK HILL | SMITHICK STEPS_CSO_FALMOUTH | 303016 | 303016 | A1 | SO on sewer network | SW 8083 3302 | 402 | #N/A | PENRYN RIVER(E) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | SMUGGLERS LANE PSEO | SMUGGLERS LANE SPS_PSCSOEO_DAWLISH | 203688 | 203688 | A1 | Storm discharge at pumping station | SX 9568 7464 | 410 | #N/A | BABBACOMBE BAY(C) |  | TEIGNMOUTH (HOLCOMBE) BEACH | Commissioned pre-2016 - full year data expected | 185.8 | 66 | 100
South West Water | SOUTH BRENT WWTW | SOUTH BRENT STW_SO_SOUTH BRENT | DRA 1062 | DRA 1062 | A2 | Inlet SO at WwTW | SX 6975 5940 | GB108046004940 | Avon - Upper | RIVER AVON | Avon |  | Commissioned in 2016 - full year data expected | 1121.54 | 61 | 100
South West Water | SOUTH MILTON STW | SOUTH MILTON STW_SSO_SOUTH MILTON | NRA-SW-3548 | NRA-SW-3548 | A3 | Storm tank at WwTW | SX 6868 4232 | 266 | #N/A | SOUTH MILTON STREAM |  | THURLESTONE (SOUTH) BEACH | Commissioned pre-2016 - full year data expected | 410.94 | 34 | 75 | Comms failure / issue | Resolved - September
South West Water | SOUTH MILTON CSO | SOUTH MILTON_CSO_SOUTH MILTON | 201717 | 201717/CS/01 | A1 | SO on sewer network | SX 6914 4269 | 266 | #N/A | STREAM (S) |  | THURLESTONE (SOUTH) BEACH | Commissioned pre-2016 - full year data expected | 2.93 | 4 | 32 | Installation set-up/design issue | Resolved - September
South West Water | SOUTH MOLTON WWTW | SOUTH MOLTON STW_SO_SOUTH MOLTON | NRA-SW-5654 | NRA-SW-5654 | A2 | Inlet SO at WwTW | SS 7225 2572 | GB108050014130 | Mole (Yeo to Burcombe Stream) | RIVER MOLE |  |  | Commissioned in 2017 - full year data expected | 1595.84 | 165 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: Cost beneficial outcome not yet determined
South West Water | SOUTH MOLTON WWTW | SOUTH MOLTON STW_SSO_SOUTH MOLTON | NRA-SW-5654 | NRA-SW-5654 | A3 | Storm tank at WwTW | SS 7225 2572 | GB108050014130 | Mole (Yeo to Burcombe Stream) | RIVER MOLE |  |  | Commissioned in 2017 - full year data expected | 759 | 74 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: Cost beneficial outcome not yet determined
South West Water | SOUTH PETHERWIN PSCSO/EO | SOUTH PETHERWIN SPS_PSCSOEO_LAUNCESTON | 301580 | 301580/PC/01 | A1 | Storm discharge at pumping station | SX 3162 8257 | GB108047007920 | Lowley Brook | LOWLEY BROOK (S) |  |  | EDM to be installed by December 2023
South West Water | SOUTH SANDS PS | SOUTH SANDS SPS_PSCSOEO_SALCOMBE | 003220/PC/01 | 003220/PC/01 | A1 | Storm discharge at pumping station | SX 7278 3766 | 430 | #N/A | COMBE STREAM |  | SALCOMBE SOUTH SANDS | Commissioned pre-2016 - full year data expected | 0.09 | 1 | 100
South West Water | SOUTH STREET CSO | SOUTH ST_CSO_HATHERLEIGH | 201772 | 201772 | A1 | SO on sewer network | SS 5405 0422 | GB108050008220 | Lower River Lew (Torridge) | RIVER LEW |  |  | Commissioned in 2017 - full year data expected | 4.97 | 18 | 100
South West Water | BELSTONE AND SOUTH TAWTON WWTW | SOUTH TAWTON STW_SSO_SOUTH TAWTON | EPRDP3221GJ | EPR/DP3221GJ | A2 | Storm tank at WwTW | SX 6477 9488 | GB108050008250 | Taw (Source to Bullow Brook) | RIVER TAW |  |  | Commissioned in 2019 - full year data expected | 2230.61 | 138 | 100
South West Water | SOUTH ZEAL PUMPING STATION | SOUTH ZEAL SPS_PSCSOEO_SOUTH ZEAL | 203707 | 203707 | A1 | Storm discharge at pumping station | SX 6545 9383 | GB108050008250 | Taw (Source to Bullow Brook) | TRIBUTARY OF RIVER TAW |  |  | Commissioned in 2018 - full year data expected | 243.31 | 40 | 100
South West Water | SOUTHMEAD CSO | SOUTHMEAD FORD STREET_MORETONHAMPSTEAD | 201756 | 201756/CS/01 | A2 | SO on sewer network | SX 7553 8628 | GB108046008330 | Wray Brook | WRAY BROOK (S) |  |  | EDM to be installed by December 2023
South West Water | SOUTHVILLE EMBANKMENT PS | SOUTHVILLE SPST_PSCSOEO_KINGSBRIDGE | 203618 | 203618 | A1 | Storm discharge at pumping station | SX 7396 4303 | 69 | #N/A | KINGSBRIDGE ESTUARY(E) | Salcombe |  | Commissioned pre-2016 - full year data expected | 9.43 | 7 | 100
South West Water | SOUTHWAY DRIVE CSO | SOUTHWAY DRIVE_CSO_PLYMOUTH | 302655 | 302655 | A1 | SO on sewer network | SX 4846 6050 | 73 | #N/A | SOUTHWAY STREAM(S) | Tamar |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 97
South West Water | SPARKWELL WASTEWATER TREATMENT WORK | SPARKWELL STW_SSO_SPARKWELL | 15/47/1/P/9 | 15/47/1/P/9 | A2 | Storm tank at WwTW | SX 5811 5701 | GB108047004000 | Silverbridge Lake | TRIBUTARY OF SILVERBRIDGE LAKE |  |  | Commissioned in 2018 - full year data expected | 2330.58 | 122 | 100
South West Water | ST AGNES WASTEWATER TREATMENT WORKS | ST AGNES STW_CSO_TRURO | 303394 | 303394 | A1 | SO on sewer network | SW 7514 5173 | 229 | #N/A | ATLANTIC OCEAN(C) |  | TREVAUNANCE COVE BEACH | Commissioned pre-2016 - full year data expected | 0.04 | 1 | 100
South West Water | ST BURYAN WWTW | ST BURYAN STW_SSO_ST BURYAN | 15/48/24/P/4 | 15/48/24/P/4 | A2 | Storm tank at WwTW | SW 4080 2520 | 270 | #N/A | TREVEDRAN STREAM |  |  | Commissioned in 2020 - full year data expected | 496.2 | 69 | 100
South West Water | ST CLEER WASTEWATER TREATMENT WORKS | ST CLEER STW_SSO_LISKEARD | 302956 | 302956 | A2 | Storm tank at WwTW | SX 2603 6791 | GB108048002320 | Seaton | TREMAR STREAM |  |  | Commissioned in 2017 - full year data expected | 1454.1 | 90 | 100
South West Water | ST CLEMENT'S HILL CSO | ST CLEMENTS HILL_CSO_TRURO | 301823 | 301823 | A1 | SO on sewer network | SW 8293 4480 | 76 | #N/A | RIVER ALLEN VIA SWS(ESTUARINE) | Fal Estuary |  | Commissioned in 2017 - full year data expected | 0.4 | 3 | 69 | Comms failure / issue | Resolved - April
South West Water | QUEEN AND RAILWAY INN CSO | ST COLUMB RD_CSO_ST COLUMB | 301877 | 301877/CS/01 | A1 | SO on sewer network | SW 9090 5927 | GB108049000230 | Gannel (Upper) | TRIB OF RIVER GANNEL |  |  | EDM to be installed by December 2023
South West Water | ST COLUMB STW | ST COLUMB STW_SSO_ST COLUMB | 303683 | 303683 | A2 | Storm tank at WwTW | SW 9081 6400 | GB108049000070 | Menalhyl | RIVER MENAHYL |  | MAWGAN PORTH BEACH | Commissioned pre-2016 - full year data expected | 60.91 | 38 | 100
South West Water | ST DENNIS WASTEWATER TREATMENT WORK | ST DENNIS STW_SO_ST DENNIS | NRA-SW-3885 | NRA-SW-3885 | A2 | Inlet SO at WwTW | SW 9411 5764 | GB108048001390 | Upper River Fal | RIVER FAL |  |  | Commissioned in 2019 - full year data expected | 113.61 | 70 | 100
South West Water | ST DENNIS WASTEWATER TREATMENT WORK | ST DENNIS STW_SSO_ST DENNIS | NRA-SW-3885 | NRA-SW-3885 | A3 | Storm tank at WwTW | SW 9411 5764 | GB108048001390 | Upper River Fal | RIVER FAL |  |  | Commissioned in 2019 - full year data expected | 7486.02 | 355 | 100
South West Water | ST DOMINICK WWTW | ST DOMINICK STW_SO_CALLINGTON | 303083 | 303083 | A2 | Inlet SO at WwTW | SX 4266 6697 | 71 | #N/A | RIVER TAMAR ESTUARY |  |  | Commissioned in 2018 - full year data expected | 1124.13 | 122 | 100
South West Water | ST DOMINICK PUMPING STATION | ST DOMINICK_PSCSOEO_SALTASH | 301636 | 301636 | A1 | Storm discharge at pumping station | SX 3976 6791 | GB108047004070 | Cotehele Stream | TRIB OF RIVER TAMAR |  |  | Commissioned in 2018 - full year data expected | 384.7 | 34 | 100
South West Water | ST GENNYS STW | ST GENNYS STW_SSO_ST GENNYS | SWWA 200 | SWWA 200 | A2 | Storm tank at WwTW | SX 1573 9596 | GB108049007190 | Crackington Stream | (S) TRIB OF CRACKINGTON STREAM |  | CRACKINGTON HAVEN BEACH | Commissioned pre-2016 - full year data expected | 23.98 | 18 | 97
South West Water | ST GEORGES ROAD (REAR OF NO16) CSO | ST GEORGES ROAD_CSO_TRURO | 302674 | 302674 | A1 | SO on sewer network | SW 8217 4493 | GB108048002340 | Kenwyn | RIVER KENWYN(S) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | ST GERMANS WWTW | ST GERMANS STW_SO_ST GERMANS | 303084 | 303084 | A2 | Inlet SO at WwTW | SX 3597 5710 | 72 | #N/A | POLBATHIC LAKE (ESTUARINE) | Lynher |  | Commissioned in 2017 - full year data expected | 700.91 | 68 | 100
South West Water | ST GILES IN THE WOOD STW | ST GILES IN THE WOOD STW_SSO_TORRINGTON | 203012 | 203012 | A2 | Storm tank at WwTW | SS 5359 1882 | GB108050014350 | Whitsleigh Down Brook | DODSCOTT BROOK(S) |  |  | EDM to be installed by December 2023
South West Water | ST GILES ON THE HEATH | ST GILES O T HEATH SPS_PSCSOEO_ST GILES | 301650 | 301650 | A1 | Storm discharge at pumping station | SX 3602 8997 | GB108047008030 | Tamar (River Ottery to River Deer) | TRIBUTARY OF THE RIVER TAMAR |  |  | EDM to be installed by December 2023
South West Water | ST JOHN STW | ST JOHN S T SEPTNK_SO_ST JOHN | 302135 | 302135/CS/01 | A2 | Inlet SO at WwTW | SX 4093 5471 | 72 | #N/A | ST JOHNS LEAT (E) |  |  | Commissioned in 2019 - full year data expected | 1.5 | 4 | 100
South West Water | ST JOHNS TERRACE CSO | ST JOHNS TERRACE_CSO_TOTNES | 202242 | 202242 | A1 | SO on sewer network | SX 8005 6071 | 23 | #N/A | MALT MILL LAKE VIA SW SEWER | Dart |  | Commissioned in 2019 - full year data expected | 6.8 | 23 | 87 | Comms failure / issue | Resolved - April
South West Water | ST KATHERINE'S WAY CSO | ST KATHERINES WAY_ CSO_TOTNES | EPRDB3893NP | EPR/DB3893NP | A1 | SO on sewer network | SX 8057 6019 | 23 | #N/A | RIVER DART ESTUARY VIA SWS | Dart |  | Commissioned in 2019 - full year data expected | 7.67 | 20 | 94
South West Water | ST KEVERNE STW | ST KEVERNE STW_SSO_ST KEVERNE | 15/48/231/P/19 | 15/48/231/P/19 | A2 | Storm tank at WwTW | SW 7900 2140 | 404 | #N/A | (S) ST KEVERNE STREAM |  | PORTHOUSTOCK BEACH | Commissioned pre-2016 - full year data expected | 436.61 | 51 | 100
South West Water | ST KEYNE NO.1 PSCSO/EO | ST KEYNE MAIN SPST_PSCSOEO_ST KEYNE | 301665 | 301665/PC/01 | A1 | Storm discharge at pumping station | SX 2410 6070 | GB108048001440 | East Looe River | WEST LOOE RIVER (S) |  |  | EDM to be installed by December 2023
South West Water | ST LEONARDS WWTW | ST LEONARDS STW_SO_LAUNCESTON | NRA-SW-6981 | NRA-SW-6981 | A2 | Inlet SO at WwTW | SX 3510 8499 | GB108047007940 | Tamar (River Ottery to River Lyd) | RIVER TAMAR |  |  | Commissioned in 2018 - full year data expected | 118.71 | 32 | 100
South West Water | ST LEONARDS WWTW | ST LEONARDS STW_SSO_LAUNCESTON | NRA-SW-6981 | NRA-SW-6981 | A3 | Storm tank at WwTW | SX 3510 8499 | GB108047007940 | Tamar (River Ottery to River Lyd) | RIVER TAMAR |  |  | Commissioned in 2018 - full year data expected | 380.89 | 29 | 100
South West Water | ST LUKES CHURCH CSO | ST LUKES CHURCH_CSO_BUCKFASTLEIGH | 201802 | 201802 | A1 | SO on sewer network | SX 7393 6600 | GB108046005190 | Dean Burn | DEAN BURN |  |  | Commissioned in 2020 - full year data expected | 6.5 | 13 | 93
South West Water | ST MABYN WWTW | ST MABYN STW_SO_ST MABYN | NRA-SW-0414 | NRA-SW-0414 | A2 | Inlet SO at WwTW | SX 0422 7540 | GB108049007050 | Allen | RIVER ALLEN |  |  | Commissioned in 2017 - full year data expected | 19.36 | 8 | 99
South West Water | ST MARTINS CRESCENT CSO | ST MARTINS CRESCENT_CSO_CAMBORNE | 301812 | 301812 | A1 | SO on sewer network | SW 6389 4081 | GB108049000600 | Red River (Upper) | TRIB OF THE RED RIVER VIA SWS |  |  | Commissioned in 2020 - full year data expected | 5 | 10 | 87 | Comms failure / issue | Resolved - April
South West Water | ST MARYCHURCH ROAD CSO | ST MARYCHURCH RD_CSO_NEWTON ABBOT | 203342 | 203342 | A1 | SO on sewer network | SX 8711 7081 | GB108046005350 | Aller Brook (Teign) - Lower | ALLER BROOK(S) | Teign |  | Commissioned pre-2016 - full year data expected | 179.05 | 29 | 100
South West Water | ST MAWES NO.1 PS | ST MAWES No1 SPS_PSCSOEO_ST MAWES | 302830 | 302830 | A1 | Storm discharge at pumping station | SW 8467 3292 | 402 | #N/A | CARRICK ROADS(E) |  |  | Commissioned pre-2016 - full year data expected | 32.99 | 30 | 100
South West Water | ST MERRYN COMBINED SEWER OVERFLOW | ST MERRYN_CSO_ST MERRYN | 300592 | 300592/CS/01 | A1 | SO on sewer network | SW 8684 7607 | 233 | #N/A | MOTHER IVEYS BAY (C) |  | HARLYN BAY BEACH | Commissioned pre-2016 - full year data expected | 617.82 | 53 | 96
South West Water | CHAPEL CAR PARK PSCSO/EO | ST NEOT SPS_PSCSOEO_LISKEARD | 301638 | 301638/PC/01 | A1 | Storm discharge at pumping station | SX 1848 6781 | GB108048007640 | St Neot River | RIVER LOVENY (S) |  |  | EDM to be installed by December 2023
South West Water | ST SIDWELLS SCHOOL CSO | ST SIDWELL'S SCH_CSO_EXETER | 201374 | 201374 | A1 | SO on sewer network | SX 9147 9250 | GB108045009040 | Exe (Creedy to Estuary) | HIGHER LEAT VIA SW SEWER | Exe |  | Commissioned in 2019 - full year data expected | 0 | 0 | 89 | Comms failure / issue | Resolved - April
South West Water | ST TEATH WASTEWATER TREATMENT WORKS | ST TEATH STW_SO_ST TEATH | 302142 | 302142 | A2 | Inlet SO at WwTW | SX 0592 8059 | GB108049007050 | Allen | TRIB OF RIVER ALLEN |  |  | Commissioned in 2017 - full year data expected | 101.94 | 112 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
South West Water | ST THOMAS ROAD CSO | ST THOMAS RD_CSO_LAUNCESTON | 301851 | 301851 | A1 | SO on sewer network | SX 3288 8510 | GB108047007960 | Kensey | RIVER KENSEY |  |  | Commissioned in 2016 - full year data expected | 2.34 | 5 | 100
South West Water | COLUMB MAJOR CSO | ST. COLUMB MAJOR_CSO_ST COLUMB | 301680 | 301680 | A1 | SO on sewer network | SW 9168 6399 | GB108049000070 | Menalhyl | RIVER MENATHYL |  |  | Commissioned in 2020 - full year data expected | 3.53 | 6 | 100
South West Water | 146 ST. PANCRAS AVENUE CSO | ST. PANCRAS AVENUE_CSO_PLYMOUTH | 301722 | 301722 | A1 | SO on sewer network | SX 4763 5804 | 73 | #N/A | TRIB OF HAM BROOK |  |  | Commissioned in 2018 - full year data expected | 4.17 | 11 | 93
South West Water | STATION ROAD PSEO | STATION RD SPST_PSCSOEO_NEWTON ST CYRES | 202844 | 202844 | A1 | Storm discharge at pumping station | SX 8810 9856 | GB108045009070 | Lower Creedy | RIVER CREEDY(S) |  |  | EDM to be installed by December 2023
South West Water | STATION ROAD CSO | STATION RD_CSO_IVYBRIDGE | 201860 | 201860 | A1 | SO on sewer network | SX 6361 5648 | GB108046005200 | Erme | RIVER ERM (S) |  | MOTHECOMBE BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | STATION ROAD PUMPING STATION | STATION ROAD SPS_PSCSOEO_PERRANPORTH | 300038/PC/01 | 300038/PE/01 | A1 | Storm discharge at pumping station | SW 7609 5419 | GB108049000700 | Bolingey Stream | BOLINGEY STREAM |  | PERRANPORTH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | TAMERTON FOLIOT PUMPING STATION | STATION ROAD SPS_PSCSOEO_PLYMOUTH | 302657 | 302657 | A1 | Storm discharge at pumping station | SX 4668 6089 | 73 | #N/A | TAMERTON LAKE(E) | Tamar |  | Commissioned pre-2016 - full year data expected | 75.75 | 21 | 100
South West Water | GPO EXCHANGE SSO | STATION ROAD_CSO_MORETONHAMPSTEAD | 203568 | 203568 | A1 | SO on sewer network | SX 7542 8560 | GB108046008330 | Wray Brook | THE WADLEY BROOK(S) |  |  | EDM to be installed by December 2023
South West Water | STAVERTON WWTW | STAVERTON STW_SSO_STAVERTON | NRA-SW-0257 | NRA-SW-0257 | A2 | Storm tank at WwTW | SX 7963 6363 | GB108046008350 | Dart | RIVER DART |  |  | Commissioned in 2019 - full year data expected | 47.33 | 13 | 100
South West Water | STEWARD COTTAGES SSO | STEWARDS COTTAGES_CSO_MORETONHAMPSTEAD | NRA-SW-5469 | NRA-SW-5469 | A1 | SO on sewer network | SX 7656 8523 | GB108046008330 | Wray Brook | THE WRAY BROOK |  |  | EDM to be installed by December 2023
South West Water | STIBB CROSS STW | STIBB CROSS STW_SO_TORRINGTON | NRA-SW-1558 | NRA-SW-1558 | A2 | Inlet SO at WwTW | SS 4285 1476 | GB108050014250 | Combe Lake | TRIB. OF COMBE LAKE |  |  | EDM to be installed by December 2023
South West Water | STOCKLAND STW | STOCKLAND STW_SSO_STOCKLAND | DRA 1435 | DRA 1435 | A3 | Storm tank at WwTW | ST 2490 0408 | GB108045015130 | Yarty | WATERCOURSE |  |  | EDM to be installed by December 2023
South West Water | STOKE CANON PSEO | STOKE CANON SPST_PSCSOEO_STOKE CANON | 201510 | 201510 | A1 | Storm discharge at pumping station | SX 9370 9756 | GB108045014970 | Lower Culm | R CULM (S) |  |  | EDM to be installed by December 2023
South West Water | STOKE CLIMSLAND STW | STOKE CLIMSLAND STW_SO_STOKE CLIMSLAND | NRA-SW-6743 | NRA-SW-6743 | A2 | Inlet SO at WwTW | SX 3585 7400 | GB108047007860 | Lower River Tamar | (S) LUCKETT STREAM |  |  | Commissioned in 2018 - full year data expected | 271.36 | 75 | 100
South West Water | STOKE GABRIEL PSCSO/EO | STOKE GABRIEL SPS_PSCSOEO_TOTNES | 202852 | 202852 | A1 | Storm discharge at pumping station | SX 8477 5691 | 23 | #N/A | RIVER DART ESTUARY(E) | Dart |  | Commissioned pre-2016 - full year data expected | 45.57 | 13 | 100
South West Water | STOKE HILL WWTW | STOKE HILL STW_SO_CRAPSTONE | 302908 | 302908 | A2 | Inlet SO at WwTW | SX 5057 6729 | 73 | #N/A | MILTON STREAM |  |  | Commissioned in 2017 - full year data expected | 3179.46 | 190 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: Cost beneficial outcome not yet determined
South West Water | STOKE HILL WWTW | STOKE HILL STW_SSO_CRAPSTONE | 302908 | 302908 | A3 | Storm tank at WwTW | SX 5057 6729 | 73 | #N/A | MILTON STREAM |  |  | Commissioned in 2017 - full year data expected | 2856.26 | 145 | 100 |  |  | Performance - Infiltration | Scheduled | Stage 1b: Confirmed "asset maintenance" issue
South West Water | STOKE MEADOW CLOSE PUMPING STATION | STOKE MEADOW CLOSE SPS_PSCSOEO_EXETER | 201630 | 201630 | A1 | Storm discharge at pumping station | SX 9330 9462 | GB108045009050 | North Brook (East Devon) | MINCINGLAKE STREAM VIA SWS |  |  | Commissioned in 2016 - full year data expected | 20.49 | 11 | 100
South West Water | STOKE RIVERS STW | STOKE RIVERS STW_SO_STOKE RIVERS | 202208 | 202208/CS/01 | A2 | Inlet SO at WwTW | SS 6303 3533 | GB108050019920 | Chelfham Stream | TRIBUTARY OF RIVER YEO(S) |  |  | EDM to be installed by December 2023
South West Water | STOKEINTEIGNHEAD PUMPING STATION | STOKEINTEIGNHEAD SPS_PSCSOEO_N ABBOT | 203091 | 203091 | A1 | Storm discharge at pumping station | SX 9140 7076 | 22 | #N/A | THE ARCH BROOK (S) | Teign |  | Commissioned pre-2016 - full year data expected | 21.98 | 16 | 100
South West Water | STONE CROSS CSO | STONE CROSS_CSO_BOVEY TRACEY | 201733 | 201733/CS/01 | A1 | SO on sewer network | SX 7403 8382 | GB108046008320 | Upper Bovey | STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | STONEPARK CRESCENT | STONEPARK CRESCENT_CSO_ASHBURTON | 202969 | 202969 | A1 | SO on sewer network | SX 7534 6935 | GB108046005270 | Ashburn | RIVER ASHBURN VIA SWS |  |  | Commissioned in 2019 - full year data expected | 97.46 | 44 | 100
South West Water | STONEYFORD PUMPING STATION | STONEYFORD SPS_PSCSOEO_CULLOMPTON | 201612 | 201612 | A1 | Storm discharge at pumping station | ST 0288 0745 | GB108045014970 | Lower Culm | RIVER KEN |  |  | Commissioned in 2020 - full year data expected | 1349.81 | 86 | 100
South West Water | STRATTON PS | STRATTON SPS_PSCSOEO_BUDE | 301150 | 301150/PC/01 | A1 | Storm discharge at pumping station | SS 2290 0549 | GB108049013730 | Upper River Strat | RIVER NEET(S) |  | SUMMERLEAZE | Commissioned pre-2016 - full year data expected | 94.09 | 26 | 100
South West Water | STRETE WWTW | STRETE STW_SO_DARTMOUTH | 203410 | 203410 | A2 | Inlet SO at WwTW | SX 8451 4667 | 260 | #N/A | START BAY, ENGLISH CHANNEL |  |  | Commissioned in 2019 - full year data expected | 264.66 | 53 | 100
South West Water | SUMMERHILL PUMPING STATION | SUMMERHILL SPS_PSCSOEO_ILSINGTON | 201582 | 201582 | A1 | Storm discharge at pumping station | SX 8191 7448 | GB108046008440 | Liverton Brook | LIVERTON BROOK | Teign |  | Commissioned in 2016 - full year data expected | 1306.94 | 86 | 100
South West Water | SUNGIRT LANE CSO | SUNGIRT LANE_CSO_LISKEARD | 303471 | 303471 | A1 | SO on sewer network | SX 2528 6414 | GB108048001440 | East Looe River | TRIBUTARY OF EAST LOOE RIVER |  | EAST LOOE BEACH | Commissioned pre-2016 - full year data expected | 43.22 | 26 | 100
South West Water | SUNNYSIDE TANK CSO | SUNNYSIDE TANK_CSO_REDRUTH | 300704 | 300704 | A1 | SO on sewer network | SW 6916 4283 | GB108049000620 | Portreath Stream | REDRUTH STREAM |  |  | Commissioned in 2019 - full year data expected | 2.63 | 6 | 84 | Comms failure / issue | Resolved - April
South West Water | SWALLOWFIELDS CSO | SWALLOWFIELDS_CSO_TOTNES | 202964 | 202964 | A1 | SO on sewer network | SX 8010 6123 | 23 | #N/A | RIVER DART ESTUARY (E) | Dart |  | Commissioned in 2019 - full year data expected | 30.1 | 18 | 43 | Comms failure / issue | N/A - Ongoing investigation
South West Water | SWANPOOL PSCSO/EO | SWANPOOL SPS_PSCSOEO_FALMOUTH | 301668 | 301668/PC/01 | A1 | Storm discharge at pumping station | SW 8003 3168 | 402 | #N/A | SWANPOOL (S) |  | SWANPOOL BEACH | Commissioned pre-2016 - full year data expected | 0.11 | 1 | 100
South West Water | SWANVALE PUMPING STATION | SWANVALE SPS_PSCSOEO_FALMOUTH | 301669 | 301669 | A1 | Storm discharge at pumping station | SW 8048 3056 | 402 | #N/A | FALMOUTH BAY/TRIB BICKLAND WAT |  | SWANPOOL BEACH | Commissioned pre-2016 - full year data expected | 28.38 | 12 | 100
South West Water | SWEETBRIER LANE CSO | SWEETBRIER LANE_CSO_EXETER | 202099 | 202099 | A1 | SO on sewer network | SX 9481 9260 | GB108045009050 | North Brook (East Devon) | NORTHBROOK | Exe |  | Commissioned in 2017 - full year data expected | 22.46 | 18 | 100
South West Water | VILLAGE HALL PUMPING STATION | SWIMBRIDGE SPS_PSCSOEO_SWIMBRIDGE | 203708 | 203708 | A1 | Storm discharge at pumping station | SS 6184 2994 | GB108050014620 | Venn | THE VENN RIVER | Taw/Torridge |  | Commissioned in 2016 - full year data expected | 58.83 | 52 | 100
South West Water | TABERNACLE STREET CSO | TABERNACLE ST_CSO_TRURO | 301696 | 301696 | A1 | SO on sewer network | SW 8269 4471 | GB108048002340 | Kenwyn | RIVER KENWYN VIA SWS | Fal Estuary |  | Commissioned in 2017 - full year data expected | 0.24 | 2 | 100
South West Water | TADDIPORT BRIDGE PUMPING STATION | TADDIPORT SPS_PSCSOEO_TORRINGTON | 200075 | 200075 | A1 | Storm discharge at pumping station | SS 4878 1870 | GB108050014660 | Torridge (Lew to Estuary) | RIVER TORRIDGE | Taw/Torridge |  | Commissioned in 2016 - full year data expected | 72.47 | 21 | 100
South West Water | TALATON PUMPING STATION | TALATON SPS_PSCSOEO_TALATON | 201650 | 201650 | A1 | Storm discharge at pumping station | SY 0685 9982 | GB108045008860 | Upper Clyst | TRIBUTARY OF RIVER CLYST |  |  | Commissioned in 2020 - full year data expected | 45.79 | 16 | 100
South West Water | TALATON WASTEWATER TREATMENT WORKS | TALATON STW_SO_TALATON | SWWA 2064 | SWWA 2064 | A2 | Inlet SO at WwTW | SY 0765 9855 | GB108045009200 | Tale | TRIB OF RIVER TALE |  |  | Commissioned in 2019 - full year data expected | 1981.82 | 118 | 100
South West Water | TAMAR WAY CSO | TAMAR WAY_CSO_PLYMOUTH | 302619 | 302619 | A1 | SO on sewer network | SX 4625 5847 | 73 | #N/A | HONICKNOWLE STREAM(S) | Tamar |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 52 | Comms failure / issue | Resolved - June
South West Water | TAMERTON CLOSE PSEO | TAMERTON CLOSE SPS_PSCSOEO_PLYMOUTH | 302656 | 302656 | A1 | Storm discharge at pumping station | SX 4625 6052 | 73 | #N/A | TAMERTON LAKE(E) | Tamar |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 96
South West Water | TAN LANE PUMPING STATION | TAN LANE SPS_PSCSOEO_EXETER | 201629 | 201629 | A1 | Storm discharge at pumping station | SX 9204 9135 | GB108045009020 | Alphin Brook | TRIB OF THE ALPHIN BROOK | Exe |  | Commissioned pre-2016 - full year data expected | 1.55 | 3 | 100
South West Water | TATWORTH WWTW | TATWORTH STW_SO_TATWORTH | 203249 | 203249 | A2 | Inlet SO at WwTW | ST 3368 0481 | GB108045014820 | Forton Brook | FORTON BROOK |  |  | Commissioned in 2018 - full year data expected | 249.89 | 54 | 95.07
South West Water | TATWORTH WWTW | TATWORTH STW_SSO_TATWORTH | 203249 | 203249 | A3 | Storm tank at WwTW | ST 3371 0479 | GB108045014820 | Forton Brook | FORTON BROOK |  |  | Commissioned in 2018 - full year data expected | 1968.61 | 135 | 100
South West Water | TAXI RANK 1 COMBINED SEWER OVERFLOW | TAXI RANK 1_CSO_OKEHAMPTON | 201728 | 201728 | A1 | SO on sewer network | SX 5889 9522 | GB108050008100 | East Okemont River | EAST OKEMENT RIVER |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 56 | Comms failure / issue | Resolved - April
South West Water | TEHIDY TERRACE CSO | TEHIDY TERRACE_CSO_FALMOUTH | 303012 | 303012 | A1 | SO on sewer network | SW 8026 3388 | 402 | #N/A | PENRYN RIVER(E) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 2.69 | 9 | 100
South West Water | TEIGN VILLAGE WWTW | TEIGN VILLAGE STW_SO_TEIGN VALLEY | NRA-SW-6737 | NRA-SW-6737 | A2 | Inlet SO at WwTW | SX 8481 8118 | GB108046008540 | Teign (Lower) | RIVER TEIGN | Teign |  | Commissioned in 2017 - full year data expected | 711.37 | 125 | 100
South West Water | HOLCOMBE PUMPING STATION | TEIGNMOUTH ROAD_PSCSOEO_HOLCOMBE | 202110 | 202110 | A1 | Storm discharge at pumping station | SX 9608 7534 | 410 | #N/A | SHELL COVE, LYME BAY(C) |  | CORYTON COVE DAWLISH | Commissioned pre-2016 - full year data expected | 146.56 | 30 | 100
South West Water | TEMPLE ROAD CSO | TEMPLE RD_CSO_EXETER | 201924 | 201924 | A1 | SO on sewer network | SX 9223 9188 | GB108045009040 | Exe (Creedy to Estuary) | RIVER EXE VIA SWS | Exe |  | Commissioned in 2018 - full year data expected | 39.37 | 28 | 100
South West Water | TEMPLE STREET CSO | TEMPLE ST_CSO_SIDMOUTH | 201828 | 201828 | A1 | SO on sewer network | SY 1296 8857 | GB108045009160 | Sid | RIVER SID |  |  | Commissioned in 2019 - full year data expected | 0.83 | 5 | 66 | Comms failure / issue | Resolved - September
South West Water | CREEKAVOSE PUMPING STATION | TERRAS SPS_PSCSOEO_ST STEPHEN | NRA-SW-3945 | NRA-SW-3945 | A1 | Storm discharge at pumping station | SW 9346 5340 | GB108048001390 | Upper River Fal | RIVER FAL |  |  | EDM to be installed by December 2023
South West Water | TEXTILE MILL | TEXTILE MILL_CSO_DARTINGTON | 202967 | 202967 | A1 | SO on sewer network | SX 7908 6202 | GB108046005160 | Bidwell Brook | BIDWELL BROOK | Dart |  | Commissioned in 2017 - full year data expected | 203.48 | 34 | 35 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | THANCKES PARK PUMPING STATION | THANKES PARK SPST_PSCSOEO_TORPOINT | 301643 | 301643 | A1 | Storm discharge at pumping station | SX 4353 5555 | 72 | #N/A | RIVER TAMAR (ESTUARINE) |  |  | Commissioned in 2016 - full year data expected | 62.57 | 60 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
South West Water | BRIDGERULE PSCSO/EO | THE BRIDGE SPS_PSCSOEO_BRIDGERULE | 301647 | 301647/PC/01 | A1 | Storm discharge at pumping station | SS 2725 0260 | GB108047008050 | Tamar (Small Brook to River Deer) | RIVER TAMAR (S) |  |  | EDM to be installed by December 2023
South West Water | NORTH ROCK SEWAGE PUMPING STATION | THE CLEAVE SPS_PSCSOEO_NORTH ROCK | 301905 | 301905/PC/01 | A1 | Storm discharge at pumping station | SX 4360 5056 | 400 | #N/A | CAWSAND BAY (C) |  | KINGSAND BEACH | Commissioned pre-2016 - full year data expected | 1.06 | 5 | 100
South West Water | COBB GATE PUMPING STATION | THE COBB SPS_PSCSOEO_LYME REGIS | 3965 | 3965 | A1 | Storm discharge at pumping station | SY 3384 9143 | 268 | #N/A | LYME BAY (C) |  | LYME REGIS FRONT BEACH | Commissioned pre-2016 - full year data expected | 22.34 | 18 | 100
South West Water | THE GREEN TANK CSO | THE GREEN TANK_CSO_BUDLEIGH SALTERTON | 200113/CS/01 | 200113/CS/01 | A1 | SO on sewer network | SY 0617 8199 | 408 | #N/A | KNOWLE STREAM |  | BUDLEIGH SALTERTON BEACH | Commissioned pre-2016 - full year data expected | 11.82 | 9 | 73 | Power failure / issue | Resolved - April
South West Water | THE GREEN COMBINED SEWER OVERFLOW | THE GREEN_CSO_OTTERTON | 201842 | 201842 | A1 | SO on sewer network | SY 0793 8529 | 18 | #N/A | RIVER OTTER |  |  | Commissioned in 2019 - full year data expected | 27.33 | 14 | 100
South West Water | THE HAM PS TANK & CSO - SIDMOUTH | THE HAM SPST_PSCSOEO_SIDMOUTH | 200835 | 200835/PC/01 | A1 | Storm discharge at pumping station | SY 1288 8732 | GB108045009160 | Sid | (S) RIVER SID AND (C) LYME BAY |  | SIDMOUTH (TOWN) BEACH | Commissioned pre-2016 - full year data expected | 1028 | 74 | 100
South West Water | THE HAM PS TANK & CSO - SIDMOUTH | THE HAM SPST_PSCSOEO_SIDMOUTH | 200835 | 200835/PC/01 | A1 | Storm discharge at pumping station | SY 1288 8732 | GB108045009160 | Sid | (S) RIVER SID AND (C) LYME BAY |  | SIDMOUTH (TOWN) BEACH | Commissioned pre-2016 - full year data expected | 62.88 | 35 | 100
South West Water | THE HAM PS TANK & CSO - SIDMOUTH | THE HAM SPST_PSCSOEO_SIDMOUTH | 200835 | 200835/PC/01 | A1 | Storm discharge at pumping station | SY 1317 8690 | GB108045009160 | Sid | (S) RIVER SID AND (C) LYME BAY |  | SIDMOUTH (TOWN) BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | THE LIZARD PUMPING STATION | THE LIZARD SPST_PSCSOEO_CHURCH COVE | 302944 | 302944 | A1 | Storm discharge at pumping station | SW 7204 1276 | 404 | #N/A | ENGLISH CHANNEL (CHURCH COVE ) |  |  | Commissioned in 2018 - full year data expected | 388.99 | 43 | 100
South West Water | MONUMENT ROAD CSO | THE MONUMENT_CSO_HELSTON | 033996/CS/01 | 33996 | A1 | SO on sewer network | SW 6553 2731 | GB108048001172 | Lower River Cober | RIVER COBER VIA SWS |  |  | Commissioned in 2016 - full year data expected | 7.29 | 2 | 97
South West Water | THE QUAY COMBINED SEWER OVERFLOW | THE QUAY_CSO_CALSTOCK | 301834 | 301834 | A1 | SO on sewer network | SX 4356 6855 | 71 | #N/A | RIVER TAMAR (ESTUARINE) |  |  | Commissioned in 2018 - full year data expected | 166.52 | 31 | 100
South West Water | CAWSAND SOUTH PUMPING STATION | THE SQUARE CAWSAND_PSCSOEO_CAWSAND | 301904 | 301904 | A1 | Storm discharge at pumping station | SX 4342 5016 | 400 | #N/A | CAWSAND BAY ESTAURINE VIA SWS |  | CAWSAND BAY | Commissioned pre-2016 - full year data expected | 203.81 | 29 | 100
South West Water | THE STRAND CSO | THE STRAND_CSO_BUDE | 301832 | 301832/CS/01 | A1 | SO on sewer network | SS 2091 0618 | GB108049007280 | Lower River Strat | RIVER NEET (S) |  | SUMMERLEAZE | Commissioned pre-2016 - full year data expected | 0.74 | 5 | 100
South West Water | THE WALRONDS CSO | THE WALDRONS NO 101_CSO_TIVERTON | 201824 | 201824 | A1 | SO on sewer network | SS 9526 1191 | GB108045015050 | Exe (Barle to Culm) | RIVER EXE |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 100
South West Water | THE WARREN PUMPING STATION | THE WARREN SPST_PSCSOEO_BIGBURY ON SEA | 202603 | 202603 | A1 | Storm discharge at pumping station | SX 6478 4440 | 266 | #N/A | BIGBURY BAY (C) |  | BIGBURY-ON-SEA (NORTH) BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | THOMPSONS TRANSPORT CSO | THOMPSONS TRANSPORT_CSO_MORETONHAMPSTEAD | 201755 | 201755/CS/01 | A1 | SO on sewer network | SX 7583 8569 | GB108046008330 | Wray Brook | WADLEY BROOK (S) |  |  | EDM to be installed by December 2023
South West Water | THORNCOMBE WWTW | THORNCOMBE STW_SSO_THORNCOMBE | NRA-SW-3897 | NRA-SW-3897 | A2 | Storm tank at WwTW | ST 3820 0376 | GB108045014840 | Upper Axe | RIVER SYNDERFORD |  |  | Commissioned in 2019 - full year data expected | 15.15 | 13 | 100
South West Water | THORNTON HILL CSO | THORNTON HILL_CSO_EXETER | 201916 | 201916 | A1 | SO on sewer network | SX 9147 9250 | GB108045009040 | Exe (Creedy to Estuary) | HIGHER LEAT VIA SWS | Exe |  | Commissioned in 2017 - full year data expected | 0 | 0 | 100
South West Water | THORVERTON WWTW | THORVERTON STW_SSO_THORVERTON | DRA 1355 | DRA 1355 | A2 | Storm tank at WwTW | SS 9359 0168 | GB108045015050 | Exe (Barle to Culm) | (S) RIVER EXE |  |  | Commissioned in 2019 - full year data expected | 11.11 | 4 | 100
South West Water | THROWLEIGH STW | THROWLEIGH STW_SO_THROWLEIGH | 202211 | 202211/CS/01 | A2 | Inlet SO at WwTW | SX 6760 9055 | GB108046008580 | Blackaton Brook | UNNAMED WATERCOURSE(S) |  |  | EDM to be installed by December 2023
South West Water | TINTAGEL CASTLE ROAD PUMP STATION | TINTAGEL CASTLE ROAD_PSCSOEO_TINTAGEL | NPSWQD008114 | NPSWQD008114 | A1 | Storm discharge at pumping station | SX 0540 8935 | 234 | #N/A | ATLANTIC OCEAN |  |  | EDM to be installed by December 2023
South West Water | TINWOOD COMBINED SEWER OVERFLOW | TINWOOD_CSO_SPARKWELL | 301876 | 301876 | A1 | SO on sewer network | SX 5816 5732 | GB108047004000 | Silverbridge Lake | TRIB OF SILVERBRIDGE LAKE |  |  | Commissioned in 2019 - full year data expected | 7.47 | 17 | 88 | Comms failure / issue | Resolved - April
South West Water | TIPTON ST JOHN PUMPING STATION | TIPTON ST JOHN SPS_CSOEO_SIDMOUTH | 201651 | 201651 | A1 | SO on sewer network | SY 0899 9174 | GB108045009170 | Lower River Otter | RIVER OTTER |  |  | Commissioned in 2016 - full year data expected | 47.98 | 22 | 100
South West Water | TIVERTON STW | TIVERTON STW_SSO_TIVERTON | 201437 | 201437 | A2 | Storm tank at WwTW | SS 9530 1030 | GB108045015050 | Exe (Barle to Culm) | RIVER EXE |  |  | Commissioned in 2019 - full year data expected | #N/A | #N/A | 0 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | TOLSKITHEY LANE CSO | TOLSKITHY LANE_CSO_REDRUTH | 301685 | 301685 | A1 | SO on sewer network | SW 6813 4249 | GB108049000620 | Portreath Stream | TRIB OF PORTREATH STREAM |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 90
South West Water | TOLVADDON DOWNS CSO | TOLVADDON TANK_CSO_REDRUTH | 301807 | 301807 | A1 | SO on sewer network | SW 6571 4169 | GB108049000600 | Red River (Upper) | TOLVADDON STREAM (S) |  | GWITHIAN TOWANS & GODREVY | Commissioned pre-2016 - full year data expected | 192.46 | 45 | 100
South West Water | TOPSHAM ROAD JCT ROBERS ROAD CSO | TOPSHAM RD/ROBERTS RD_CSO_EXETER | 201926 | 201926 | A1 | SO on sewer network | SX 9223 9189 | GB108045009040 | Exe (Creedy to Estuary) | RIVER EXE VIA SWS | Exe |  | Commissioned in 2018 - full year data expected | 0 | 0 | 100
South West Water | TOR PARK ROAD PUMPING STATION | TOR PARK SPS_PSCSOEO_PAIGNTON | 201625 | 201625 | A1 | Storm discharge at pumping station | SX 8656 5928 | 23 | #N/A | YALBERTON STREAM VIA SWS | Dart |  | Commissioned in 2016 - full year data expected | 8.72 | 9 | 100
South West Water | TORBRIDGE NORTH CSO | TORBRIDGE NORTH_CSO_YEALMPTON | 301895 | 301895 | A1 | SO on sewer network | SX 5791 5157 | GB108047004010 | Lower River Yealm | RIVER YEALM | Yealm |  | Commissioned in 2018 - full year data expected | 0.03 | 1 | 94
South West Water | TORBRIDGE SOUTH CSO | TORBRIDGE SOUTH_CSO_YEALMPTON | 301896 | 301896 | A1 | SO on sewer network | SX 5792 5156 | GB108047004010 | Lower River Yealm | RIVER YEALM | Yealm |  | Commissioned in 2018 - full year data expected | 7.97 | 11 | 96
South West Water | TORBRYAN PS | TORBRYAN SPST_PSCSOEO_TORBRYAN | 203002 | 203002 | A1 | Storm discharge at pumping station | SX 8232 6669 | GB108046005210 | Am Brook | HALWELL STREAM(S) |  |  | EDM to be installed by December 2023
South West Water | TORCROSS PUMPING STATION | TORCROSS SPST_PSCSOEO_TORCROSS | 203035 | 203035 | A1 | Storm discharge at pumping station | SX 8241 4170 | 260 | #N/A | START BAY (C) | Start Bay | SLAPTON SANDS (TORCROSS) | Commissioned pre-2016 - full year data expected | 895.56 | 58 | 100
South West Water | TORPOINT WASTEWATER TREATMENT WORKS | TORPOINT STW_SO_TORPOINT | NRA-SW-6990 | NRA-SW-6990 | A2 | Inlet SO at WwTW | SX 4147 5405 | 72 | #N/A | ST JOHN'S LAKE (ESTUARINE) |  |  | Commissioned pre-2016 - full year data expected | 266.37 | 43 | 100
South West Water | MILL STREET COMBINED SEWER OVERFLOW | TORRIDGE INN MILL STREET_CSO_TORRINGTON | 200081/CS/01 | 200081 | A1 | SO on sewer network | SS 4878 1873 | GB108050014660 | Torridge (Lew to Estuary) | RIVER TORRIDGE | Taw/Torridge |  | Commissioned in 2018 - full year data expected | 1.1 | 11 | 100
South West Water | TORRIDGE MOUNT CSO | TORRIDGE MOUNT_CSO_BIDEFORD | 2880 | 2880 | A1 | SO on sewer network | SS 4558 2626 | 199 | #N/A | RIVER TORRIDGE VIA SWS |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 100
South West Water | TORRIDGE VALE DAIRIES CSO | TORRIDGE VALE DAIRIES_CSO_TORRINGTON | EPRYB3093NU | EPR/YB3093NU | A1 | SO on sewer network | SS 4857 1872 | GB108050014660 | Torridge (Lew to Estuary) | RIVER TORRIDGE | Taw/Torridge |  | Commissioned in 2018 - full year data expected | 42.31 | 45 | 100
South West Water | TORRINGTON STREET PS | TORRINGTON STREET SPS_PSCSOEO_BIDEFORD | 203122 | 203122 | A1 | Storm discharge at pumping station | SS 4551 2608 | 199 | #N/A | RIVER TORRIDGE ESTUARY (E) | Taw/Torridge |  | Commissioned in 2018 - full year data expected | 31 | 21 | 100
South West Water | TORRINGTON WWTW | TORRINGTON STW_SO_TORRINGTON | 203792 | 203792 | A2 | Inlet SO at WwTW | SS 4819 1917 | GB108050014660 | Torridge (Lew to Estuary) | RIVER TORRIDGE | Taw/Torridge |  | Commissioned in 2016 - full year data expected | 14.49 | 4 | 100
South West Water | TORRINGTON WWTW | TORRINGTON STW_SSO_TORRINGTON | 203792 | 203792 | A3 | Storm tank at WwTW | SS 4818 1922 | GB108050014660 | Torridge (Lew to Estuary) | RIVER TORRIDGE | Taw/Torridge |  | Commissioned in 2016 - full year data expected | 620.16 | 44 | 100
South West Water | TOTNES STW | TOTNES STW_SO_TOTNES | 203080 | 203080 | A2 | Inlet SO at WwTW | SX 8071 6101 | 23 | #N/A | DART ESTUARY(E) | Dart |  | Commissioned pre-2016 - full year data expected | 935.59 | 104 | 100
South West Water | TOTNES TOWN PUMPING STATION | TOTNES TOWN SPST_PSCSOEO_TOTNES | 201662 | 201662 | A1 | Storm discharge at pumping station | SX 8066 6053 | 23 | #N/A | RIVER DART (ESTUARINE) | Dart |  | Commissioned pre-2016 - full year data expected | 585.85 | 107 | 100
South West Water | TOWAN HEAD PUMPING STATION | TOWAN HEAD SPS_PSCSOEO_NEWQUAY | 301322 | 301322/PC/01 | A1 | Storm discharge at pumping station | SW 8008 6297 | 231 | #N/A | ATLANTIC OCEAN(T) |  | FISTRAL NORTH & SOUTH | Commissioned pre-2016 - full year data expected | 62.5 | 33 | 100
South West Water | PARSONAGE COTTAGE HILL CSO | TOWN HILL_CSO_ERMINGTON | 201874 | 201874 | A1 | SO on sewer network | SX 6373 5282 | GB108046005040 | Lower Erme | RIVER ERME |  | MOTHECOMBE BEACH | Commissioned pre-2016 - full year data expected | 170.13 | 23 | 100
South West Water | TOWN PARK PUMPING STATION | TOWN PARK SPS_PSCSOEO_TORRINGTON | 200083 | 200083 | A1 | Storm discharge at pumping station | SS 4909 1959 | GB108050014660 | Torridge (Lew to Estuary) | TRIB. OF COMMON LAKE STREAM | Taw/Torridge |  | Commissioned in 2016 - full year data expected | 113.95 | 80 | 86 | Comms failure / issue | Resolved - May
South West Water | TOWN QUAY PUMPING STATION | TOWN QUAY SPST_PSCSOEO_FOWEY | 302775 | 302775 | A1 | Storm discharge at pumping station | SX 1266 5166 | 26 | #N/A | RIVER FOWEY ESTUARY (E) | Fowey | READYMONEY COVE | Commissioned pre-2016 - full year data expected | 349.32 | 156 | 100
South West Water | TOWNSTAL TANK CSO | TOWNSTAL TANK_CSO_DARTMOUTH | 202395 | 202395 | A1 | SO on sewer network | SX 8654 5177 | 23 | #N/A | TRIB OF OLD MILL CREEK VIA SWS | Dart |  | Commissioned in 2019 - full year data expected | 69.76 | 15 | 100
South West Water | TRACEY COURT CSO | TRACEY CT/WESTERN APPR_CSO_PLYMOUTH | 301787 | 301787 | A1 | SO on sewer network | SX 4697 5400 | 73 | #N/A | MILLBAY DOCKS VIA SWS (EST) |  |  | Commissioned in 2016 - full year data expected | 4.93 | 1 | 100
South West Water | TRACK CSO | TRACK LEADING TO STW_CSO_SALCOMBE REGIS | 201840 | 201840/CS/01 | A1 | SO on sewer network | SY 1473 8854 | 408 | #N/A | STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | TREDENHAM CLOSE CSO | TREDENHAM CLOSE_CSO_PAR | EPRYB3993NQ | EPR/YB3993NQ | A1 | SO on sewer network | SX 0731 5368 | GB108048002290 | Par River (Lower) | ST BLAZEY STREAM | St.Austell Bay | PAR SANDS | Commissioned in 2016 - full year data expected | 1.62 | 3 | 98
South West Water | TREDINNICK STW | TREDINNICK STW_SO_TREDINNICK | 302138 | 302138/CS/01 | A2 | Inlet SO at WwTW | SX 2352 5734 | GB108048002000 | West Looe River | UN-NAMED WATERCOURSE (S) |  |  | EDM to be installed by December 2023
South West Water | TREDRIZZICK BRIDGE PUMPING STATION | TREDRIZZICK SPS_PSCSOEO_TREDRIZZICK | 34546 | 034546/PC/01 | A1 | Storm discharge at pumping station | SW 9588 7703 | 135 | #N/A | (S) POLZEATH STREAM |  | POLZEATH BEACH | Commissioned pre-2016 - full year data expected | 61.84 | 13 | 100
South West Water | TREFIUS PARK COMBINED SEWER OVERFLO | TREFUSIS PARK_CSO_PLYMOUTH | 301709 | 301709 | A1 | SO on sewer network | SX 4938 5585 | 73 | #N/A | TRIBUTARY OF THE RIVER PLYM |  | PLYMOUTH HOE (EAST) | Commissioned in 2018 - full year data expected | 61.55 | 64 | 100
South West Water | TREGADILLET PS | TREGADILLET SPS_PSCSOEO_LAUNCESTON | 301625 | 301625 | A1 | Storm discharge at pumping station | SX 2985 8498 | GB108047007960 | Kensey | RIVER KENSEY |  |  | Commissioned in 2019 - full year data expected | 15.16 | 5 | 100
South West Water | TREGONY BRIDGE PUMPING STATION | TREGONY SPST_PSCSOEO_TREGONY | 301657 | 301657 | A1 | Storm discharge at pumping station | SW 9207 4473 | GB108048001270 | Lower River Fal | RIVER FAL | Fal Estuary |  | Commissioned in 2016 - full year data expected | 45.64 | 18 | 100
South West Water | TREHEMBORNE PS | TREHEMBOURNE SPS_PSCSOEO_ST MERRYN | 300016 | 300016 | A1 | Storm discharge at pumping station | SW 8720 7330 | 231 | #N/A | TREYARNON STREAM |  |  | Commissioned in 2020 - full year data expected | 0.63 | 2 | 100
South West Water | TREKNOW STW | TREKNOW STW_SSO_TREBARWITH | CRA 1 | CRA 1 | A2 | Storm tank at WwTW | SX 0548 8648 | 234 | #N/A | (S) TREBARWITH STREAM |  | TREBARWITH STRAND BEACH | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | TRELANDER HIGHWAY CSO | TRELANDER HIGHWAY_CSO_TRURO | 302681 | 302681 | A1 | SO on sewer network | SW 8292 4479 | 76 | #N/A | RIVER ALLEN(ESTUARINE) VIA SWS | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 15.12 | 28 | 100
South West Water | TREVENEAGUE GRDNS PLAYING FIELD CSO | TREVENEAGUE GARDENS_CSO_PLYMOUTH | 301725 | 301725 | A1 | SO on sewer network | SX 4796 5784 | 73 | #N/A | TRIB OF HAM BROOK |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 88 | Comms failure / issue | Resolved - April
South West Water | LOWER TREVILLA PUMPING STATION | TREVILLA SPS_PSCSOEO_FEOCK | 301596 | 301596 | A1 | Storm discharge at pumping station | SW 8255 3887 | 76 | #N/A | PILL CREEK | Fal Estuary |  | Commissioned in 2016 - full year data expected | 178.27 | 22 | 100
South West Water | TREVONE PUMPING STATION | TREVONE SPST_PSCSOEO_PADSTOW | 300014 | 300014/PC/01 | A1 | Storm discharge at pumping station | SW 8864 7605 | 233 | #N/A | TREVONE BAY |  | TREVONE BAY BEACH | Commissioned pre-2016 - full year data expected | 372.01 | 21 | 100
South West Water | TREWIDLAND STW | TREWIDLAND STW_SO_TREWIDLAND | 302140 | 302140/CS/01 | A2 | Inlet SO at WwTW | SX 2510 5981 | GB108048001440 | East Looe River | EAST LOOE RIVER (S) |  |  | EDM to be installed by December 2023
South West Water | TROON FARM CSO | TROON 1&2_CSO_TROON | 301810 | 301810/CS/01 | A1 | SO on sewer network | SW 6584 3815 | GB108049000560 | Roseworthy Stream | RED RIVER (S) |  |  | EDM to be installed by December 2023
South West Water | TURLAKE SPS | TURLAKE SPS_PSCSOEO_EXETER | 202177 | 202177/PC/01 | A1 | Storm discharge at pumping station | SX 9049 9619 | GB108045009070 | Lower Creedy | TRIB OF R EXE |  |  | EDM to be installed by December 2023
South West Water | TURNCHAPEL BARRACKS PUMPING STATION | TURNCHAPEL BARRACKS SPS_PSCSOEO_PLYMOUTH | 032895/PC/01 | 32895 | A1 | Storm discharge at pumping station | SX 4945 5322 | 73 | #N/A | CATTEWATER (ESTUARINE) |  | PLYMOUTH HOE (EAST) | Commissioned in 2016 - full year data expected | 45.54 | 28 | 100
South West Water | TURNCHAPEL SLIPWAY PUMPING STATION | TURNCHAPEL SLIPWAY SPS_PSCSOEO_PLYMOUTH | 032896/PC/01 | 32896 | A1 | Storm discharge at pumping station | SX 4933 5309 | 73 | #N/A | CATTEWATER (ESTUARINE) |  | PLYMOUTH HOE (EAST) | Commissioned in 2016 - full year data expected | 30.57 | 26 | 98
South West Water | UFFCULME PUMPING STATION | UFFCULME SPS_PSCSOEO_UFFCULME | 203111 | 203111 | A1 | Storm discharge at pumping station | ST 0632 1196 | GB108045014970 | Lower Culm | RIVER CULM |  |  | Commissioned in 2018 - full year data expected | 41.44 | 22 | 100
South West Water | UFFCULME WWTW | UFFCULME STW_SSO_UFFCULME | SWWA 6 | SWWA 6 | A2 | Storm tank at WwTW | ST 0622 1186 | GB108045014970 | Lower Culm | RIVER CULM |  |  | Commissioned in 2018 - full year data expected | 231.21 | 43 | 100
South West Water | UPLOWMAN STW | UPLOWMAN STW_SO_TIVERTON | 203806 | 203806 | A2 | Inlet SO at WwTW | ST 0132 1527 | GB108045015030 | Lowman | UPLOWMAN STREAM |  |  | Commissioned in 2018 - full year data expected | 484.72 | 26 | 100
South West Water | LYME REGIS (UPLYME) STW | UPLYME STW_SSO_UPLYME | 3269 | 3269 | A2 | Storm tank at WwTW | SY 3338 9329 | GB108044009760 | Lim | TRIBUTARY OF THE RIVER LIM |  | LYME REGIS CHURCH CLIFF BEACH | Commissioned pre-2016 - full year data expected | 468.54 | 30 | 100
South West Water | UPTON CROSS COMBINED SEWER OVERFLOW | UPTON CROSS_CSO_RILLA MILL | 301891 | 301891 | A1 | SO on sewer network | SX 2861 7266 | GB108047007670 | Lower River Lynher | TRIB OF RIVER LYNER |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 78 | Comms failure / issue | Resolved - July
South West Water | VALLEY VIEW PSCSO/EO | VALLEY VIEW SPS_PSCSOEO_ST KEYNE | 301637 | 301637/PC/01 | A1 | Storm discharge at pumping station | SX 2407 6093 | GB108048001440 | East Looe River | EAST LOOE RIVER (S) |  |  | EDM to be installed by December 2023
South West Water | VELATOR BRIDGE CSO | VELATOR BRIDGE BRAUNTON_CSO_BARNSTAPLE | 203286 | 203286 | A1 | SO on sewer network | SS 4858 3570 | 198 | #N/A | KNOWL WATER TRIB OF TIDAL CAEN | Taw/Torridge |  | Commissioned pre-2016 - full year data expected | 10.3 | 13 | 100
South West Water | VELATOR PUMPING STATION | VELATOR SPST_PSCSOEO_BRAUNTON | 203430 | 203430 | A1 | Storm discharge at pumping station | SS 4854 3540 | 198 | #N/A | TIDAL RIVER CAEN(E) | Taw/Torridge | INSTOW BEACH | Commissioned pre-2016 - full year data expected | 61.81 | 50 | 100
South West Water | VENTURA CSO | VENTURA_EXETER ROAD_CSO_HONITON | 201848 | 201848/CS/01 | A1 | SO on sewer network | ST 1502 0026 | GB108045009180 | Middle River Otter | DITCH |  |  | EDM to be installed by December 2023
South West Water | DAWLISH BREAKWATER SSO | VIADUCT SPS_PSCSOEO_DAWLISH | 200824 | 200824/PC/01 | A1 | Storm discharge at pumping station | SX 9648 7651 | 406 | #N/A | LYME BAY (C) |  | DAWLISH (TOWN) BEACH | Commissioned pre-2016 - full year data expected | 20.29 | 21 | 100
South West Water | VICARAGE ROAD CSO | VICARAGE RD_CSO_SIDMOUTH | 201832 | 201832 | A1 | SO on sewer network | SY 1277 8806 | GB108045009160 | Sid | RIVER SID VIA SWS |  |  | Commissioned in 2019 - full year data expected | 0.7 | 3 | 100
South West Water | VICTORIA LODGE PS CSO/EO | VICTORIA LODGE SPS_PSCSOEO_MALPAS | 302827 | 302827 | A1 | Storm discharge at pumping station | SW 8414 4251 | 76 | #N/A | TRURO RIVER ESTUARY SYSTEM(E) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 222.55 | 13 | 100
South West Water | VICTORIA PARK CSO | VICTORIA PARK UPPER_CSO_PLYMOUTH | 301766 | 301766 | A1 | SO on sewer network | SX 4622 5441 | 73 | #N/A | STONEHOUSE CREEK VIA SWS (EST) |  |  | Commissioned pre-2016 - full year data expected | 2.72 | 8 | 100
South West Water | VICTORIA QUAY PSCSO/EO | VICTORIA QUAY SPST_PSCSOEO_MALPAS | 302828 | 302828 | A1 | Storm discharge at pumping station | SW 8438 4257 | 76 | #N/A | (E) TRURO & TRESILLIAN RVRS | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | VICTORIA PSCSO/EO | VICTORIA SPS_PSCSOEO_ROCHE | 301631 | 301631/PC/01 | A1 | Storm discharge at pumping station | SW 9915 6148 | GB108048002310 | Par River (Upper) | RIVER CAMEL (S) |  |  | EDM to be installed by December 2023
South West Water | VICTORIA SQUARE CSO | VICTORIA SQUARE_CSO_TRURO | 2894/5 | 2894/5 | A1 | SO on sewer network | SW 8250 4481 | GB108048002340 | Kenwyn | RIVER KENWYN | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 37.05 | 29 | 100
South West Water | ST MAWGAN PSCSO/EO | VILLAGE SPS_PSCSO_ST MAWGAN | 301611 | 301611 | A1 | SO on sewer network | SW 8725 6600 | GB108049000070 | Menalhyl | RIVER MENALHYL (S) |  | MAWGAN PORTH BEACH | Commissioned pre-2016 - full year data expected | 3.21 | 1 | 100
South West Water | WADEBRIDGE PS | WADEBRIDGE SPST_PSCSOEO_WADEBRIDGE | 302977 | 302977 | A1 | Storm discharge at pumping station | SW 9885 7272 | 135 | #N/A | CAMEL ESTUARY(E) | Camel |  | Commissioned in 2017 - full year data expected | 204.59 | 24 | 100
South West Water | WAR MEMORIAL PSCSO/EO | WAR MEMORIAL SPS_PSCSOEO_ALTARNUN | 301598 | 301598/PC/01 | A1 | Storm discharge at pumping station | SX 2238 8133 | GB108047007700 | Penpont Water | PENEONT WATER (S) |  |  | EDM to be installed by December 2023
South West Water | WAR MEMORIAL CSO | WAR MEMORIAL_CSO_CULMSTOCK | 201853 | 201853/CS/01 | A1 | SO on sewer network | ST 0973 1369 | GB108045014980 | Middle Culm | RIVER CULM (S) |  |  | EDM to be installed by December 2023
South West Water | WARFLEET CREEK PUMPING STATION | WARFLEET CREEK SPS_PSCSOEO_DARTMOUTH | 202402 | 202402 | A1 | Storm discharge at pumping station | SX 8828 5053 | 23 | #N/A | RIVER DART ESTUARY | Dart |  | Commissioned in 2016 - full year data expected | 344 | 358 | 100 |  |  | Data collection - Tidal / river inundation | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue
South West Water | PUMPING STATION AT WARREN POINT | WARREN POINT SPS_PSCSOEO_BIGBURY | 202604 | 202604 | A1 | Storm discharge at pumping station | SX 6490 4457 | 266 | #N/A | BIGBURY BAY (COASTAL) |  | CHALLABOROUGH BEACH | Commissioned pre-2016 - full year data expected | 0.33 | 3 | 100
South West Water | DAWLISH WARREN ROAD PS | WARREN ROAD SPS_PSCSOEO_DAWLISH | 202631 | 202631 | A1 | Storm discharge at pumping station | SX 9761 7892 | 20 | #N/A | SHUTTERTON BROOK(S) | Exe |  | Commissioned pre-2016 - full year data expected | 97.42 | 63 | 100
South West Water | WATERGATE BAY PUMPING STATION | WATERGATE SPS_PSCSOEO_WATERGATE BAY | 301320 | 301320/PC/01 | A1 | Storm discharge at pumping station | SW 8423 6493 | 231 | #N/A | STREAM/ATLANTIC OCEAN (S) |  | WATERGATE BAY | Commissioned pre-2016 - full year data expected | 216.86 | 13 | 100
South West Water | WATERLEAT PARK PSCSO/EO | WATERLEAT PARK SPS_PSCSOEO_HONITON | 202180/PC/01 | 202180/PC/01 | A1 | Storm discharge at pumping station | ST 1691 0018 | GB108045009180 | Middle River Otter | TRIB OF RIVER OTTER |  |  | EDM to be installed by December 2023
South West Water | WATERSIDE PUMPING STATION | WATERSIDE No1 SPST_PSCSOEO_SALTASH | 301482 | 301482/PC/01 | A1 | Storm discharge at pumping station | SX 4326 5854 | 71 | #N/A | RIVER TAMAR ESTUARY(E) | Tamar |  | Commissioned pre-2016 - full year data expected | 13.19 | 14 | 100
South West Water | WATERY LANE CSO | WATERY LANE_CSO_GREAT TORRINGTON | 200078/CS/01 | 200078 | A1 | SO on sewer network | SS 4992 1886 | GB108050014660 | Torridge (Lew to Estuary) | CASTLE HILL STREAM VIA SWS | Taw/Torridge |  | Commissioned in 2017 - full year data expected | 0 | 0 | 100
South West Water | WEARE GIFFARD WWTW | WEARE GIFFARD STW_SO_WEARE GIFFARD | 202222 | 202222 | A2 | Inlet SO at WwTW | SS 4718 2204 | 199 | #N/A | RIVER TORRIDGE | Taw/Torridge |  | Commissioned in 2017 - full year data expected | 2128.57 | 182 | 100
South West Water | WEAVER CRESCENT CSO | WEAVER CRESCENT_CSO_TIVERTON | 201961 | 201961 | A1 | SO on sewer network | SS 9481 1241 | GB108045015050 | Exe (Barle to Culm) | RIVER EXE |  |  | Commissioned in 2017 - full year data expected | 222.25 | 44 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: Cost beneficial outcome not yet determined
South West Water | WEBBER STREET CSO | WEBBER ST_CSO_FALMOUTH | 303018 | 303018 | A1 | SO on sewer network | SW 8083 3302 | 402 | #N/A | PENRYN RIVER(E) | Fal Estuary |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | WELL STREET CSO | WELL ST_CSO_EXETER | 201371 | 201371 | A1 | SO on sewer network | SX 9147 9250 | GB108045009040 | Exe (Creedy to Estuary) | HIGHER LEAT VIA SW SEWER | Exe |  | Commissioned in 2017 - full year data expected | 124.99 | 48 | 100
South West Water | WEMBURY BEACH PSCSO/EO | WEMBURY BEACH SPST_PSCSOEO_WEMBURY | 301660 | 301660/PC/01 | A1 | Storm discharge at pumping station | SX 5174 4852 | 262 | #N/A | WEMBURY BAY (C) |  | WEMBURY BEACH | Commissioned pre-2016 - full year data expected | 9.37 | 9 | 93
South West Water | WATERY LANE CSO | WEMBURY STW_SSO_WEMBURY | 200078/CS/01 | 32738 | A2 | Storm tank at WwTW | SX 5098 4832 | 262 | #N/A | CASTLE HILL STREAM VIA SWS |  |  | Commissioned in 2018 - full year data expected | 747.89 | 49 | 100
South West Water | WEMBWORTHY STW | WEMBWORTHY NEW STW_SO_WEMBWORTHY | 203835 | 203835 | A2 | Inlet SO at WwTW | SS 6605 1003 | GB108050014210 | Taw (River Yeo to Little Dart River) | THE LABDON STREAM(S) |  |  | EDM to be installed by December 2023
South West Water | WEST ALVINGTON CSO | WEST ALVINGTON_CSO_W ALVINGTON | 203417 | 203417 | A1 | SO on sewer network | SX 7265 4357 | 69 | #N/A | KINGSBRIDGE ESTUARY(S) | Salcombe |  | Commissioned pre-2016 - full year data expected | 12.55 | 29 | 100
South West Water | WEST BANK PUMPING STATION | WEST BANK SPS_PSCSOEO_OTTERY ST MARY | 201380 | 201380 | A1 | Storm discharge at pumping station | SY 0929 9508 | GB108045009170 | Lower River Otter | TRIB OF RIVER OTTER |  |  | Commissioned in 2016 - full year data expected | 82.21 | 12 | 100
South West Water | WEST CHARLETON STW | WEST CHARLETON_SSO_KINGSBRIDGE | 203206 | 203206 | A2 | Storm tank at WwTW | SX 7520 4235 | 69 | #N/A | CHARLETON STREAM(S) | Salcombe |  | Commissioned in 2017 - full year data expected | 386.42 | 41 | 100
South West Water | WEST CLIFF COMBINED SEWER OVERFLOW | WEST CLIFF PK/LAMBETH WK_CSO_DAWLISH | 200822 | 200822/CS/01 | A1 | SO on sewer network | SX 9569 7671 | GB108045008910 | Dawlish Water | DAWLISH WATER (S) |  | DAWLISH (TOWN) BEACH | Commissioned pre-2016 - full year data expected | 4.35 | 9 | 100
South West Water | WEST HOE PUMPING STATION | WEST HOE TANKS SPS_PSCSOEO_PLYMOUTH | 300616/PE/01 | 300616 | A1 | Storm discharge at pumping station | SX 4719 5357 | 73 | #N/A | PLYMOUTH SOUND (E) |  | PLYMOUTH HOE (WEST) | Commissioned pre-2016 - full year data expected | 4.43 | 7 | 100
South West Water | WEST HOE TUNNEL SHAFT 5B.2 | WEST HOE TANKS SPS_PSCSOEO_PLYMOUTH | 300453/PC/01 | 300453 | A1 | Storm discharge at pumping station | SX 4718 5357 | 73 | #N/A | PLYMOUTH SOUND |  | PLYMOUTH HOE (WEST) | Commissioned pre-2016 - full year data expected | 4.43 | 7 | 100
South West Water | WEST LOOE SQUARE CSO | WEST LOOE QUAY_CSO_LOOE | 300974 | 300974 | A1 | SO on sewer network | SX 2540 5323 | 74 | #N/A | LOOE RIVER (HARBOUR) (E) |  | EAST LOOE BEACH | Commissioned pre-2016 - full year data expected | 1198.62 | 141 | 100
South West Water | WEST STREET PUMPING STATION | WEST STREET SPS_PSCSOEO_SOUTH MOLTON | 201619 | 201619 | A1 | Storm discharge at pumping station | SS 7093 2567 | GB108050013950 | Nadrid Water | TRIBUTARY OF NADRID WATER |  |  | Commissioned in 2018 - full year data expected | 34.98 | 24 | 100
South West Water | WEST STREET PUMPING STATION | WEST STREET SPS_PSCSOEO_SOUTH MOLTON | 201619 | 201619 | A1 | Storm discharge at pumping station | SS 7093 2567 | GB108050013950 | Nadrid Water | TRIBUTARY OF NADRID WATER |  |  | Commissioned in 2018 - full year data expected | 34.98 | 24 | 100
South West Water | SIPHON TELEPHONE BOX CSO | WESTBRIDGE COTTS_CSO_TAVISTOCK | 202240/CS/01 | 202240 | A1 | SO on sewer network | SX 4769 7337 | GB108047007840 | Lower River Tavy | RIVER TAVY |  |  | Commissioned in 2016 - full year data expected | 170.57 | 55 | 74 | Comms failure / issue | Resolved - July | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
South West Water | WESTCOMBE LANE CSO | WESTCOMBE LN_CSO_BIDEFORD | 203291 | 203291 | A1 | SO on sewer network | SS 4528 2702 | GB108050014500 | Kenwith Stream | KENWITH STREAM(S) | Taw/Torridge |  | Commissioned in 2016 - full year data expected | 0 | 0 | 100
South West Water | WESCOTS QUAY CSO | WESTCOTS QUAY TANK_CSO_ST IVES | 301691 | 301691/CS/01 | A1 | SO on sewer network | SW 5185 4041 | 230 | #N/A | ST IVES BAY (C) |  | PORTHMINSTER BEACH ST.IVES | Commissioned pre-2016 - full year data expected | 2.19 | 7 | 100
South West Water | WEST CROFT ROAD | WESTCROFT_CSO_HOLSWORTHY | SWWA 2228 | SWWA 2228 | A1 | SO on sewer network | SS 3388 0367 | GB108047013880 | Deer | RIVER DEER |  |  | EDM to be installed by December 2023
South West Water | WESTEXE PUMPING STATION | WESTEXE SPST_PSCSOEO_TIVERTON | 203079 | 203079 | A1 | Storm discharge at pumping station | SS 9532 1201 | GB108045015050 | Exe (Barle to Culm) | RIVER EXE |  |  | Commissioned in 2018 - full year data expected | 1872.33 | 123 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: Cost beneficial outcome not yet determined
South West Water | WESTLEIGH PUMPING STATION | WESTLEIGH SPS_PSCSOEO_BIDEFORD | 200201 | 200201/PC/01 | A1 | Storm discharge at pumping station | SS 4681 2896 | 198 | #N/A | RIVER TORRIDGE ESTUARY(E) |  | INSTOW BEACH | Commissioned pre-2016 - full year data expected | 202.13 | 23 | 100
South West Water | WESTON MILL CEMETERY TANK CSO | WESTON MILL CEMETERY_CSO_PLYMOUTH | 302611 | 302611 | A1 | SO on sewer network | SX 4557 5773 | 73 | #N/A | WESTON MILL STREAM(E) | Tamar |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | WESTON PUMPING STATION | WESTON SPS_PSCSOEO_HONITON | 202181 | 202181 | A1 | Storm discharge at pumping station | ST 1422 0006 | GB108045009170 | Lower River Otter | RIVER OTTER |  |  | Commissioned in 2017 - full year data expected | 134.8 | 18 | 100
South West Water | WESTVILLE/TACKETWOOD PS | WESTVILLE SPST_PSCSOEO_KINGSBRIDGE | 203422 | 203422 | A1 | Storm discharge at pumping station | SX 7340 4366 | 69 | #N/A | KINGSBRIDGE ESTUARY(E) | Salcombe |  | Commissioned pre-2016 - full year data expected | 131.2 | 9 | 100
South West Water | WHITEHOUSE SLIP (POINT) CSO | WHITEHSE SLIP POINT_CSO_FOWEY | 302773 | 302773 | A1 | SO on sewer network | SX 1235 5140 | 26 | #N/A | RIVER FOWEY ESTUARY(E) | Fowey | READYMONEY COVE | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | WHITFORD ROAD COMBINED SEWER O/F | WHITFORD ROAD_CSO_MUSBURY | SWWA 115 | SWWA 115 | A1 | SO on sewer network | SY 2625 9506 | GB108045008870 | Lower Axe | RIVER AXE |  |  | Commissioned in 2018 - full year data expected | 10.67 | 3 | 100
South West Water | WHITLEIGH WOOD CSO | WHITLEIGH WOOD_CSO_PLYMOUTH | 302854 | 302854 | A1 | SO on sewer network | SX 4764 6039 | 73 | #N/A | TRIBUTARY OF TAMERTON LAKE(S) | Tamar |  | Commissioned pre-2016 - full year data expected | 24.52 | 22 | 100
South West Water | WIDECOMBE STW | WIDECOMBE STW_SO_WIDECOMBE IN THE MOOR | 203911 | 203911 | A2 | Inlet SO at WwTW | SX 7190 7659 | GB108046008390 | East Webburn River | EAST WEBBURN RIVER(S) |  |  | EDM to be installed by December 2023
South West Water | WIDEGATES WWTW | WIDEGATES STW_SO_LOOE | SWWA 1003 | SWWA 1003 | A2 | Inlet SO at WwTW | SX 2860 5736 | GB108048002320 | Seaton | TRIBUTARY OF RIVER SEATON |  |  | Commissioned in 2020 - full year data expected | 36.08 | 37 | 100
South West Water | WILLAND WASTEWATER TREATMENT WORKS | WILLAND STW_SO_WILLAND | 203113 | 203113 | A2 | Inlet SO at WwTW | ST 0419 1060 | GB108045015020 | Spratford Stream | TRIB OF RIVER CULM |  |  | Commissioned in 2018 - full year data expected | 269.5 | 71 | 100
South West Water | WILLAND WASTEWATER TREATMENT WORKS | WILLAND STW_SSO_WILLAND | 203113 | 203113 | A3 | Storm tank at WwTW | ST 0420 1016 | GB108045015020 | Spratford Stream | TRIB OF RIVER CULM |  |  | Commissioned in 2018 - full year data expected | 1027.05 | 70 | 100
South West Water | WILTON ROAD CSO | WILTON RD/ VALLETORT RD_CSO_PLYMOUTH | 301750 | 301750 | A1 | SO on sewer network | SX 4622 5441 | 73 | #N/A | STONEHOUSE CREEK VIA SWS (EST) |  |  | Commissioned in 2017 - full year data expected | 8.78 | 12 | 100
South West Water | WINSFORD PSCSO/EO | WINSFORD SPST_PSCSOEO_WINSFORD | 203228 | 203228 | A1 | Storm discharge at pumping station | SS 9072 3483 | GB108045020930 | Exe (Source to Quarme) | RIVER EXE(S) |  |  | Jan 2021 | 0 | 0 | 100
South West Water | WINSHAM WASTEWATER TREATMENT WORKS | WINSHAM STW_SO_WINSHAM | DRA 1539 | DRA 1539 | A2 | Inlet SO at WwTW | ST 3752 0599 | GB108045014840 | Upper Axe | RIVER AXE |  |  | Commissioned pre-2016 - full year data expected | 25.92 | 14 | 6 | Comms failure / issue | Resolved - December
South West Water | WINSHAM WASTEWATER TREATMENT WORKS | WINSHAM STW_SO_WINSHAM | DRA 1539 | DRA 1539 | A2 | Inlet SO at WwTW | ST 3752 0599 | GB108045014840 | Upper Axe | RIVER AXE |  |  | Commissioned pre-2016 - full year data expected | 25.92 | 14 | 6 | Comms failure / issue | Resolved - December
South West Water | WINSTON LANE CSO | WINSTON LN_CSO_BRIXTON | 302463 | 302463 | A1 | SO on sewer network | SX 5559 5188 | GB108047004000 | Silverbridge Lake | TRIB OF SILVERBRIDGE LAKE(S) | Yealm |  | Commissioned pre-2016 - full year data expected | 1.58 | 8 | 100
South West Water | WINSFORD PARK PSCSO/EO | WINSTON PARK_PSCSOEO_SOUTH MOLTON | 202184 | 202184/PC/01 | A1 | Storm discharge at pumping station | SS 7148 2621 | GB108050014130 | Mole (Yeo to Burcombe Stream) | TRIB OF RIVER MOLE |  |  | EDM to be installed by December 2023
South West Water | WOODBURY WWTW | WOODBURY_SSO_WOODBURY | 202848 | 202848 | A2 | Storm tank at WwTW | SX 9979 8678 | GB108045008980 | Polly Brook | WOODBURY BROOK | Exe |  | Commissioned in 2018 - full year data expected | 1625.88 | 92 | 100
South West Water | WOODLAND AVE CSO | WOODLAND AV_CSO_HOLCOMBE | 202488 | 202488 | A1 | SO on sewer network | SX 9509 7428 | 410 | #N/A | STREAM DIS TO LYME BAY (S) |  | TEIGNMOUTH (HOLCOMBE) BEACH | Commissioned pre-2016 - full year data expected | 70.84 | 41 | 100
South West Water | WOOLACOMBE PSCSO/EO | WOOLACOMBE SPS_PSCSOEO_WOOLACOMBE | 201678 | 201678 | A1 | Storm discharge at pumping station | SS 4508 4420 | 235 | #N/A | BRISTOL CHANNEL (C) |  | WOOLACOMBE (VILLAGE) BEACH | Commissioned pre-2016 - full year data expected | 702.99 | 43 | 100
South West Water | YARCOMBE STW | YARCOMBE STW_SO_YARCOMBE | NRA-SW-0273 | NRA-SW-0273 | A2 | Inlet SO at WwTW | ST 2472 0799 | GB108045015130 | Yarty | (S) TRIB RIVER YARTY |  |  | EDM to be installed by December 2023
South West Water | YARNSCOMBE SEWAGE TREATMENT WORKS | YARNSCOMBE STW_SO_YARNSCOMBE | 202220 | 202220/CS/01 | A2 | Inlet SO at WwTW | SS 5587 2363 | GB108050014460 | Langham Lake | LANGHAM LAKE(S) |  |  | EDM to be installed by December 2023
South West Water | YARNSCOMBE SEWAGE TREATMENT WORKS | YARNSCOMBE STW_SSO_YARNSCOMBE | 200402 | 200402/SS/02 | A3 | Storm tank at WwTW | SS 5578 2367 | GB108050014460 | Langham Lake | TRIBUTARY OF LANGHAM LAKE(S) |  |  | EDM to be installed by December 2023
South West Water | YEALMPTON WWTW | YEALMPTON STW_SO_YEALMPTON | 300436/FN/01 | 300436 | A2 | Inlet SO at WwTW | SX 5772 5148 | GB108047004010 | Lower River Yealm | RIVER YEALM | Yealm |  | Commissioned pre-2016 - full year data expected | 51.54 | 21 | 100
South West Water | YEALMPTON WWTW | YEALMPTON STW_SSO_YEALMPTON | 300436/SS/01 | 300436 | A3 | Storm tank at WwTW | SX 5768 5138 | GB108047004010 | Lower River Yealm | YEALM | Yealm |  | Commissioned pre-2016 - full year data expected | 66.61 | 8 | 100
South West Water | YELLAND PUMPING STATION | YELLAND SPS_PSCSOEO_BARNSTAPLE | 203126 | 203126 | A1 | Storm discharge at pumping station | SS 4757 3218 | 198 | #N/A | RIVER TAW ESTUARY(E) | Taw/Torridge | INSTOW BEACH | Commissioned pre-2016 - full year data expected | 13 | 29 | 100
South West Water | YELLOWSANDS PUMPING STATION | YELLOW SANDS SPS_PSCSOEO_NEWQUAY | 301323 | 301323/PC/01 | A1 | Storm discharge at pumping station | SW 7903 6174 | 231 | #N/A | ATLANTIC OCEAN (C) |  | FISTRAL NORTH & SOUTH | Commissioned pre-2016 - full year data expected | 47.52 | 31 | 100
South West Water | WEST ANSTEY STW | YEO MILL STW_SO_WEST ANSTEY | 202999 | 202999 | A2 | Inlet SO at WwTW | SS 8416 2639 | GB108050014140 | Yeo (Molland) | RIVER YEO |  |  | EDM to be installed by December 2023
South West Water | YEOFORD WASTEWATER TREATMENT WORKS | YEOFORD STW_SSO_CREDITON | NRA-SW-6626 | NRA-SW-6626 | A2 | Storm tank at WwTW | SX 7894 9874 | GB108045009240 | Upper Yeo (Creedy) | RIVER YEO |  |  | Commissioned in 2018 - full year data expected | 1711.39 | 120 | 100
South West Water | YEOLMBRIDGE PS | YEOLMBRIDGE SPST_PSCSOEO_YEOLMBRIDGE | 301651 | 301651 | A1 | Storm tank at WwTW | SX 3165 8735 | GB108047007981 | Lower River Ottery | TRIB OF RIVER OTTERY |  |  | Commissioned in 2020 - full year data expected | 304.38 | 107 | 100
South West Water | FORDER NO 1 PSCSO/EO | FORDER MAIN No1 SPS_PSCSOEO_SALTASH | 302102 | 302102 | A1 | Storm discharge at pumping station | SX4127058370 | 71 | N/A | RIVER LYNER (S) |  |  | Commissioned pre-2016 - full year data expected | 136.9 | 23 | 96
South West Water | LANIVET INN COMBINED SEWER OVERFLOW | LANIVET INN_CSO_LANIVET | 302157 | 302157 | A1 | SO on sewer network | SX0379064170 | GB108049000030 | Lanivet Stream | LANIVET STREAM |  |  | May 2021 | 0.79 | 3 | 100
South West Water | LEE MILL STW | LEE MILL STW_SO_PLYMOUTH | NRA-SW-0237 | NRA-SW-0237 | A2 | Inlet SO at WwTW | SX6032055624 | GB108047004010 | Lower River Yealm | (S) UNNAMED TRIB RIVER YEALM |  |  | Commissioned in 2019 - full year data expected | 278.13 | 135 | 100
South West Water | LIPSON VALE 2 CSO | LIPSON VALE 2_CSO_PLYMOUTH | 301775 | 301775 | A1 | SO on sewer network | SX4925655691 | GB520804714300 | PLYMOUTH TAMAR | TRIB OF THE RIVER PLYM VIA SWS |  |  | Commissioned in 2020 - full year data expected | 3.02 | 5 | 100
South West Water | MORELEIGH STW | MORELEIGH STW_SO_MORELEIGH | NRA-SW-6964 | NRA-SW-6964 | A2 | Inlet SO at WwTW | SX7646052730 | GB108046004920 | Torr Bk | (S) TRIB OF TORR BROOK |  |  | June 2021 | 352.48 | 45 | 100
South West Water | IVY COTTAGE PUMPING STATION | NEWTON ROAD_CSO_TORQUAY | 201623 | 201263 | A1 | SO on sewer network | SX8896566285 | GB108046005330 | Aller Brook (Teign) - Upper | TRIB OF ALLER BROOK |  |  | Commissioned in 2016 - full year data expected | 0.07 | 1 | 84.11 | Comms failure / issue | Resolved - August
South West Water | MOOR LANE PSCSO/EO | POLTIMORE SPS_PSCSOEO_EXETER | 201649 | 201649/PC/01 | A1 | Storm discharge at pumping station | SX9645097049 | GB108045008860 | Upper Clyst | STREAM (S) |  |  | July 2021 | 1.43 | 1 | 100
South West Water | PORTHTOWAN BEACH PSEO | PORTHTOWAN BEACH No1 SPS_PSCSOEO_PTOWAN | 301542 | 301542/PE/01 | A1 | Storm discharge at pumping station | SW6916148022 | 229 | N/A | LOCAL STREAM (S) |  | PORTHTOWAN | Commissioned pre-2016 - full year data expected | 80.56 | 9 | 100
South West Water | PRIORY SLIP PUMPING STATION | PRIORY SLIP SPS_PSCSOEO_KINGSWEAR | 200159/PC/01 | 200159 | A1 | Storm discharge at pumping station | SX8816550955 | GB510804605900 | DART | DART ESTUARY |  |  | July 2021 | 2.06 | 5 | 100
South West Water | SCORRITON STW | SCORRITON STW_SO_SCORRITON | 203887 | 203887 | A2 | Inlet SO at WwTW | SX7074068590 | GB108046008350 | Dart | HOLY BROOK(S) |  |  | July 2021 | 196.94 | 35 | 100
South West Water | ALTARNUN STW (STORM TANK) | ALTARNUN STW_SO_ALTARNUN | SWWA 154 | SWWA 154 | A2 | Inlet SO at WwTW | SX2241481301 | GB108047007700 | Penpont Water | PENPONT WATER |  |  | EDM to be installed by December 2023
South West Water | ALTARNUN STW (STORM TANK) | ALTARNUN STW_SSO_ALTARNUN | SWWA 154 | SWWA 154 | A3 | Storm tank at WwTW | SX2241481301 | GB108047007700 | Penpont Water | PENPONT WATER |  |  | Jan 2021 | 2169.6 | 155 | 100
South West Water | CSO AT ATLANTIC HOTEL | ATLANTIC HOTEL_CSO_ST MARYS | EPRBB3394VJ | EPR/BB3394VJ | A1 | SO on sewer network | SV9019510644 | GB620807080000 | Scilly Isles | ATLANTIC OCEAN |  |  | EDM to be installed by December 2023
South West Water | AYLESBEARE STW | AYLESBEARE STW_SO_AYLESBEARE | NRA-SW-3581 | NRA-SW-3581 | A2 | Inlet SO at WwTW | SY0358091860 | GB108045008730 | Aylesbeare Stream | AYLESBEARE BROOK |  |  | EDM to be installed by December 2023
South West Water | BAMPTON WWTW | BAMPTON SPST_PSCSOEO_BAMPTON | SWWA 42 | SWWA 42 | A1 | Storm discharge at pumping station | SS9544421947 | GB108045015070 | Lower Batherm | RIVER BATHERM |  |  | EDM to be installed by December 2023
South West Water | BAMPTON WWTW | BAMPTON STW_SO_BAMPTON | SWWA 42 | SWWA 42 | A2 | Inlet SO at WwTW | SS9544421947 | GB108045015070 | Lower Batherm | RIVER BATHERM |  |  | Commissioned in 2019 - full year data expected | 1050.64 | 79 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP7 or Green Recovery
South West Water | BATHPOOL STW | BATHPOOL STW_SO_BATHPOOL | 302121 | 302121/CS/01 | A2 | Inlet SO at WwTW | SX2481074690 | GB108047007680 | Withey Brook | RIVER LYNER (S) |  |  | EDM to be installed by December 2023
South West Water | BEAFORD WASTE WTW | BEAFORD STW_SO_BEAFORD | 200355/SF/01 | 200355/SF/01 | A2 | Inlet SO at WwTW | SS5528015260 | GB108050014320 | Woolleigh Brook | BEAFORD BROOK |  |  | EDM to be installed by December 2023
South West Water | BELLE PARADE CSO | BELLE PARADE_CSO_CREDITON | 201871 | 201871/CS/01 | A1 | SO on sewer network | SS8339200376 | GB108045009090 | Middle Creedy | STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | BISHOPS NYMPTON STW | BISHOPS NYMPTON STW_SO_BISHOPS NYMPTON | NRA-SW-6747 | NRA-SW-6747/SO/01 | A2 | Inlet SO at WwTW | SS7588023410 | GB108050014120 | Crooked Oak | (S) CROOKED OAK STREAM |  |  | Jan 2021 | 168.91 | 85 | 100
South West Water | BITTAFORD STW | BITTAFORD STW_SSO_BITTAFORD | DRA 1456 | DRA 1456 | A2 | Storm tank at WwTW | SX6653656552 | GB108046005110 | Lud Brook | RIVER ERME (S) |  |  | September 2021 | 0 | 0 | 100
South West Water | BLUNTS STW | BLUNTS S T STW_SO_TIDEFORD | 303338 | 303338 | A2 | Inlet SO at WwTW | SX3444062920 | GB108047007670 | Lower River Lynher | BLUNTS STREAM (S)(LYHNER TRIB) |  |  | EDM to be installed by December 2023
South West Water | BODMIN GOLF COURSE PSCSO/EO | BODMIN GOLF CLUB SPS_PSCSOEO_BODMIN | 302093 | 302093/PC/01 | A1 | Storm discharge at pumping station | SX0733464400 | GB108049000040 | St Lawrence Stream | TRIB RIVER CAMEL (S) |  |  | EDM to be installed by December 2023
South West Water | BOSORNE ROAD SEWER OVERFLOW | BOSORNE RD 2_CSOEO_ST JUST | 303091 | 303091 | A1 | SO on sewer network | SW3647031230 | 230 | N/A | ATLANTIC / PORTH NANVEN STREAM |  |  | EDM to be installed by December 2023
South West Water | BOSWEDDEN PUMPING STATION | BOSWEDDEN SPS_PSCSOEO_CAPE CORNWALL | EPRZP3626GN | EPR/ZP3626GN | A1 | Storm discharge at pumping station | SW3545831843 | GB610807680001 | Lands End to Trevose Head | ATLANTIC OCEAN |  |  | EDM to be installed by December 2023
South West Water | BOW WASTEWATER TREATMENT WORKS | BOW STW_SO_BOW | DRA 1382 | DRA 1382 | A2 | Inlet SO at WwTW | SS7156002171 | GB108050008270 | Upper River Yeo (Lapford) | RIVER YEO |  |  | November 2021 | 0 | 0 | 100
South West Water | BRADWORTHY WWTW SSO | BRADWORTHY STW_SO_BRADWORTHY | NRA-SW-1058 | NRA-SW-1058 | A2 | Inlet SO at WwTW | SS3295513516 | GB108050014270 | Waldon | TRIB OF RIVER TORRIDGE |  |  | Mar 2021 | 980.84 | 130 | 100
South West Water | BRATTON CLOVELLY WWTW CSO | BRATTON CLOVELLY STW_SO_BRATTON CLOVELY | NRA-SW-1061 | NRA-SW-1061 | A2 | Inlet SO at WwTW | SX4648091750 | GB108047008010 | Thrushel | TRIB OF RIVER THRUSHEL |  |  | EDM to be installed by December 2023
South West Water | BRATTON FLEMING STW | BRATTON FLEMING STW_SO_BRATTON FLEMING | DRA 1538 | DRA 1538 | A2 | Inlet SO at WwTW | SS6400037300 | GB108050019920 | Chelfham Stream | (S) RIVER YEO (BARNSTAPLE) |  |  | June 2021 | 0 | 0 | 100
South West Water | BRIDGERULE WWTW | BRIDGERULE STW_SO_BRIDGERULE | NRA-SW-0406 | NRA-SW-0406 | A2 | Inlet SO at WwTW | SS2702102404 | GB108047008050 | Tamar (Small Brook to River Deer) | RIVER TAMAR (S) |  |  | EDM to be installed by December 2023
South West Water | BRIDGETOWN WWTW PS | BRIDGETOWN STW_SO_BRIDGETOWN | NRA-SW-1069 | NRA-SW-1069 | A2 | Inlet SO at WwTW | SS9230033300 | GB108045020890 | Exe (Quarme to Haddeo) | RIVER EXE |  |  | July 2021 | 0 | 0 | 100
South West Water | BROADHEMPSTON WWTW CSO | BROADHEMPSTON STW_SO_BROADHEMPSTON | NRA-SW-1075 | NRA-SW-1075 | A2 | Inlet SO at WwTW | SX7995065910 | GB108046005230 | Hems - Upper | BROADHEMPSTON STREAM |  |  | Jan 2021 | 1503.28 | 303 | 100
South West Water | APPLE TREE HOUSE BROOMHILL CSO | BROOMHILL_CSO_CHAGFORD | 201801 | 201801/CS/01 | A1 | SO on sewer network | SX7072788177 | GB108046008550 | Teign (Upper) | RIVER TEIGN (S) |  |  | EDM to be installed by December 2023
South West Water | BROWNSTON STW | BROWNSTON STW_SO_LOWER BROWNSTON | 203603 | 203603 | A2 | Inlet SO at WwTW | SX6972052740 | GB108046005070 | Sheepham Bk | SHILSTON BROOK(S) |  |  | EDM to be installed by December 2023
South West Water | BUCKLAND BREWER STW | BUCKLAND BREWER STW_SO_BUCKLAND BREWER | DRA 1513 | DRA 1513 | A2 | Inlet SO at WwTW | SS4171220412 | GB108050014360 | Duntz | TRIB OF RIVER YEO (BIDEFORD) |  |  | Mar 2021 | 0 | 0 | 100
South West Water | BULLER ROAD CSO | BULLER RD_CSO_CREDITON | 201873 | 201873/CS/01 | A1 | SO on sewer network | SS8282400638 | GB108045009090 | Middle Creedy | STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | BURRINGTON CSO | BURRINGTON_CSO_BURRINGTON | 202225 | 202225/CS/01 | A1 | SO on sewer network | SS6366016810 | GB108050014310 | Mully Brook | TRIBUTARY OF RIVER TAW(S) |  |  | EDM to be installed by December 2023
South West Water | O/S 8 CALLENICK STREET CSO | CALENICK ST NO8_CSO_TRURO | 301799 | 301799/CS/01 | A1 | SO on sewer network | SW8240148808 | GB108048002360 | Zelah Brook | KENWYN RIVER (E) |  |  | EDM to be installed by December 2023
South West Water | CARGREEN PSCSO/EO | CARGREEN SPS_PSCSOEO_CARGREEN | 302094 | 302094/PC/01 | A1 | Storm discharge at pumping station | SX4361062580 | GB520804714300 | PLYMOUTH TAMAR | RIVER TAMAR (E) |  |  | EDM to be installed by December 2023
South West Water | CARGREEN CSO | CARGREEN_CSO_CARGREEN | 301837 | 301837/CS/01 | A1 | SO on sewer network | SX4361062588 | GB520804714300 | PLYMOUTH TAMAR | RIVER TAMAR (E) |  |  | EDM to be installed by December 2023
South West Water | CASTLE HOSPITAL CSO | CASTLE HOSPITAL_CSO_OKEHAMPTON | 201730 | 201730/CS/01 | A1 | SO on sewer network | SX5861594630 | GB108050008080 | West Okement | WEST OKEMENT (S) |  |  | EDM to be installed by December 2023
South West Water | CHAWLEIGH STW | CHAWLEIGH STW_SSO_CHAWLEIGH | NRA-SW-3839 | NRA-SW-3839 | A2 | Storm tank at WwTW | SS7169012800 | GB108050014340 | Lower Little River Dart | LITTLE DART RIVER |  |  | September 2021 | 120.45 | 35 | 100
South West Water | CHERITON BISHOP STW | CHERITON BISHOP STW_SO_CHERITON BISHOP | NRA-SW-3561 | NRA-SW-3561 | A2 | Inlet SO at WwTW | SX7748093690 | GB108045009230 | Ford Brook (EXE) | FORD BROOK(S) |  |  | Jan 2021 | 1.79 | 3 | 100
South West Water | CHERITON BISHOP STW | CHERITON BISHOP STW_SSO_CHERITON BISHOP | NRA-SW-3562 | NRA-SW-3562 | A3 | Storm tank at WwTW | SX7748093690 | GB108045009230 | Ford Brook (EXE) | FORD BROOK(S) |  |  | Jan 2021 | 1336.75 | 72 | 100
South West Water | CHERITON FITZPAINE WWTW | CHERITON FITZPAINE STW_SSO_CHERITON F | 202985 | 202985 | A2 | Storm tank at WwTW | SS8578806210 | GB108045014900 | Holly Water | TRIBUTARY OF HOLLY WATER |  |  | May 2021 | 3507.02 | 182 | 100
South West Water | SPENCER GARDENS CSO | CHICHESTER CRESCENT_CSO_SALTASH | EPRYB3893NY | EPR/YB3893NY | A1 | SO on sewer network | SX4234958470 | 71 | N/A | TRIB OF R. TAMAR ESTUARY (SWS) |  |  | EDM to be installed by December 2023
South West Water | CHILLATON STW | CHILLATON STW_SO_CHILLATON | 302122 | 302122/CS/01 | A2 | Inlet SO at WwTW | SX4320082420 | GB108047007710 | Quither Brook | TRIB OF RIVER LYD (S) |  |  | EDM to be installed by December 2023
South West Water | CHILLINGTON & FROGMORE STW | CHILLINGTON STW_SO_CHILLINGTON | 203442 | 203442 | A2 | Inlet SO at WwTW | SX7835242779 | GB108046004760 | Avon (DevonTidal) and Sth Hams - Frogmore | CHILLINGTON STREAM(S) |  |  | EDM to be installed by December 2023
South West Water | CHITTLEHAMPTON CSO | CHITTLEHAMPTON_CSO_UMBERLEIGH | 201951 | 201951/CS/01 | A1 | SO on sewer network | SS6367625458 | GB108050014520 | Hawkridge Brook | TRIB OF HAWKRIDGE BROOK (S) |  |  | EDM to be installed by December 2023
South West Water | CHULMLEIGH WWTW SSO | CHULMLEIGH STW_SSO_CHULMLEIGH | NRA-SW-1126 | NRA-SW-1126 | A2 | Storm tank at WwTW | SS6899113919 | GB108050014340 | Lower Little River Dart | LITTLE DART RIVER |  |  | Jan 2021 | 2242.76 | 155 | 100
South West Water | CHURCHINFORD STW | CHURCHINFORD STW_SO_CHURCHINFORD | 002728/FN/01 | 2728 | A2 | Inlet SO at WwTW | ST2178012410 | GB108045015120 | Upper River Otter | RIVER OTTER |  |  | Feb 2021 | 116.37 | 16 | 100
South West Water | COACH ROAD CSO | COACH RD GREEN_CSO_SILVERTON | 201827 | 201827/CS/01 | A1 | SO on sewer network | SS9586802909 | GB108045014970 | Lower Culm | STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | COBBATON STW | COBBATON STW_SO_COBBATON | 203881 | 203881 | A2 | Inlet SO at WwTW | SS6212026170 | GB108050014520 | Hawkridge Brook | HAWKRIDGE BROOK(S) |  |  | EDM to be installed by December 2023
South West Water | COLYTON & COLYFORD WWTW | COLYTON STW_SO_COLYTON | DRA 441 | 203431 | A2 | Inlet SO at WwTW | SY2553293012 | GB108045008870 | Lower Axe | RIVER AXE |  |  | EDM to be installed by December 2023
South West Water | COMMONMOOR STW | COMMON MOOR STW_SO_COMMON MOOR | NRA-SW-1141 | NRA-SW-1141 | A2 | Inlet SO at WwTW | SX2345069200 | GB108048007650 | Fowey (Upper) | TRIB OF RIVER FOWEY |  |  | EDM to be installed by December 2023
South West Water | COUNCIL YARD PSCSO/EO | COUNCIL YARD SPST_PSCSOEO_CREDITON | 201657 | 201657/PC/01 | A1 | Storm discharge at pumping station | SS8445000380 | GB108045009090 | Middle Creedy | TRIB RIVER CREEDY (S) |  |  | EDM to be installed by December 2023
South West Water | CROWSNEST STW | CROWS NEST STW_SO_DARITE | 302123 | 302123/CS/01 | A2 | Inlet SO at WwTW | SX2641069220 | GB108048002320 | Seaton | RIVER SEATON (S) |  |  | EDM to be installed by December 2023
South West Water | CULMSTOCK SEWAGE TREATMENT WORKS | CULMSTOCK STW_SO_CULMSTOCK | NRA-SW-3571 | NRA-SW-3571 | A2 | Inlet SO at WwTW | ST0999013590 | GB108045014980 | Middle Culm | RIVER CULM |  |  | May 2021 | 118.14 | 53 | 100
South West Water | DENBURY WASTEWATER TREATMENT WORKS | DENBURY STW_SO_DENBURY | NRA-SW-7808 | NRA-SW-7808 | A2 | Inlet SO at WwTW | SX8278668433 | GB108046005210 | Am Brook | HALWELL STREAM |  |  | Commissioned in 2020 - full year data expected | 175.65 | 63 | 100
South West Water | DENBURY WASTEWATER TREATMENT WORKS | DENBURY STW_SSO_DENBURY | NRA-SW-7808 | NRA-SW-7808 | A3 | Storm tank at WwTW | SX8278668433 | GB108046005210 | Am Brook | HALWELL STREAM |  |  | Commissioned in 2020 - full year data expected | 1642.57 | 84 | 100
South West Water | DODDISCOMBSLEIGH STW | DODDISCOMBSLEIGH STW_SO_TEIGN VALLEY | 203009 | 203009 | A2 | Inlet SO at WwTW | SX8538086920 | GB108046008540 | Teign (Lower) | DODDISCOMBSLEIGH STREAM(S) |  |  | EDM to be installed by December 2023
South West Water | DOLTON SEWAGE TREATMENT WORKS | DOLTON STW_SSO_DOLTON | 203161 | 203161 | A2 | Storm tank at WwTW | SS5741011980 | GB108050014240 | Dolton Stream | TRIB OF RIVER TORRIDGE(S) |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 100
South West Water | DREWSTEIGNTON STW | DREWSTEIGNTON STW_SO_CHAGFORD | NRA-SW-6987 | NRA-SW-6987 | A2 | Inlet SO at WwTW | SX7379091480 | GB108046008570 | Fingle Brook | FINGLE BROOK |  |  | EDM to be installed by December 2023
South West Water | EAST PRAWLE STW | EAST PRAWLE STW_SO_SALCOMBE | 202193/CS/01 | 202193/CS/01 | A2 | Inlet SO at WwTW | SX7830036410 | 260 | N/A | UNNAMED COASTAL STREAM(S) |  |  | EDM to be installed by December 2023
South West Water | EGLOSKERRY STW | EGLOSKERRY STW_SO_EGLOSKERRY | 302124 | 302124/CS/01 | A2 | Inlet SO at WwTW | SX2695086430 | GB108047007960 | Kensey | RIVER KENSEY (S) |  |  | EDM to be installed by December 2023
South West Water | LYNHER PSCSO/EO | ELIOT DRIVE SPS_PSCSOEO_ST GERMANS | 302109 | 302109/PC/01 | A1 | Storm discharge at pumping station | SX3614057041 | GB520804714300 | PLYMOUTH TAMAR | POLBATHIC LAKE (E) |  |  | EDM to be installed by December 2023
South West Water | ELLENGLAZE PSCSO/EO | ELLENGLAZE SPS_PSCSOEO_CUBERT | 302101 | 302101/PC/01 | A1 | Storm discharge at pumping station | SW7827057648 | GB108049000710 | Holywell Stream | STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | ERMINGTON STW | ERMINGTON STW_SO_ERMINGTON | NRA-SW-1188 | NRA-SW-1188 | A2 | Storm tank at WwTW | SX6336352415 | GB108046005040 | Lower Erme | RIVER ERME |  |  | Commissioned pre-2016 - full year data expected | 103.99 | 10 | 100
South West Water | EXBOURNE STW | EXBOURNE STW_SO_OKEHAMPTON | 200365/SF/01 | 200365/SF/01 | A2 | Inlet SO at WwTW | SS6055002000 | GB108050014090 | Hole Brook | (S)TRIB. OF HOLE BROOK |  |  | May 2021 | 384.23 | 79 | 97
South West Water | EXFORD STW | EXFORD STW_SO_EXFORD | NRA-SW-3496 | NRA-SW-3496 | A2 | Inlet SO at WwTW | SS8554638273 | GB108045020930 | Exe (Source to Quarme) | RIVER EXE |  |  | May 2021 | 193.73 | 20 | 100
South West Water | FALMOUTH STW INLET & STORM PS | FALMOUTH STW_SO_FALMOUTH | 302999 | 302999 | A2 | Storm tank at WwTW | SW8256032100 | GB650806250000 | Carrick Roads Outer | PENRYN RIVER(E) |  |  | Commissioned pre-2016 - full year data expected | 355.25 | 29 | 100
South West Water | FOOTBALL FIELD CSO | FOOTBALL FIELD O/S STW_CSO_SOUTH BRENT | 201719 | 201719/CS/01 | A1 | SO on sewer network | SX6983559470 | GB108046004940 | Avon - Upper | RIVER AVON (S) |  |  | EDM to be installed by December 2023
South West Water | GORRAN CHURCHTOWN STW | GORRAN CHURCHTOWN STW_SO_ST AUSTELL | 303580 | 303580 | A2 | Inlet SO at WwTW | SX0012042430 | 256 | N/A | PORTMELLON STREAM(S) |  |  | Commissioned pre-2016 - full year data expected | #N/A | #N/A | #N/A | No longer operational as an overflow - permit revoked or to be revoked
South West Water | IN FIELD R/0 11 GRANTLANDS | GRANTLANDS_CSO_UFFCULME | 201818 | 201818/CS/01 | A1 | SO on sewer network | ST0650212443 | GB108045014970 | Lower Culm | MILL BROOK (S) |  |  | EDM to be installed by December 2023
South West Water | HALWILL SEWAGE TREATMENT WORKS | HALWILL STW_SO_HALWILL | 2027 | 002027/SF/01 | A2 | Inlet SO at WwTW | SX4292099230 | GB108047008040 | Carey | (S) RIVER CAREY |  |  | May 2021 | 962.24 | 133 | 100
South West Water | HARTLAND WASTEWATER TREATMENT WORKS | HARTLAND STW_SO_HARTLAND | NRA-SW-6967 | NRA-SW-6967 | A2 | Inlet SO at WwTW | SS2534724592 | GB108050014050 | Abbey River | ABBEY RIVER |  |  | EDM to be installed by December 2023
South West Water | HATHERLEIGH STW | HATHERLEIGH STW_SSO_HATHERLEIGH | SWWA 153 | SWWA 153 | A2 | Storm tank at WwTW | SS5382004098 | GB108050008220 | Lower River Lew (Torridge) | RIVER LEW (S) |  |  | Commissioned in 2020 - full year data expected | 1306.88 | 207 | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP7 or Green Recovery
South West Water | HAWKCHURCH STW | HAWKCHURCH STW_SO_HAWKCHURCH | SWWA 2412 | SWWA 2412 | A2 | Inlet SO at WwTW | ST3406000880 | GB108045008850 | Blackwater River | BLACKWATER RIVER/STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | HEMYOCK WASTEWATER TREATMENT WORKS | HEMYOCK STW_SO_HEMYOCK | 202474 | 202474 | A2 | Inlet SO at WwTW | ST1358013720 | GB108045014980 | Middle Culm | RIVER CULM |  |  | Feb 2021 | 26.75 | 8 | 76 | Sensor failure / issue | Resolved - June
South West Water | HIGH BICKINGTON STW | HIGH BICKINGTON STW_SO_HIGH BICKINGTON | 202194/CS/01 | 202194/CS/01 | A2 | Inlet SO at WwTW | SS5951020280 | GB108050014460 | Langham Lake | TRIBUTARY OF LANGHAM LAKE(S) |  |  | May 2021 | 684.88 | 95 | 100
South West Water | HUNTSHAM STW | HUNTSHAM STW_SO_HUNTSHAM | 202196/CS/01 | 202196/CS/01 | A2 | Inlet SO at WwTW | ST0043020260 | GB108045015030 | Lowman | TRIBUTARY OF RIVER LOWMAN(S) |  |  | EDM to be installed by December 2023
South West Water | JUBILEE STREET CSO | JUBILEE STREET_CSO_AVETON GIFFORD | 202384 | 202384 | A1 | SO on sewer network | SX6938047650 | 24 | N/A | RIVER AVON (S) |  |  | Commissioned pre-2016 - full year data expected | #N/A | #N/A | #N/A | No longer operational as an overflow - permit revoked or to be revoked
South West Water | LOWER KELLY PSCSO/EO | KELLY_PSCSOEO_CALSTOCK | 301613 | 301613/PC/01 | A1 | Storm discharge at pumping station | SX4342468651 | GB520804714300 | PLYMOUTH TAMAR | RIVER TAMAR (E) |  |  | EDM to be installed by December 2023
South West Water | KINGS NYMPTON (SOUTH) WWTW SSO | KINGS NYMPTON SOUTH STW_SO_KINGS NYMPTON | NRA-SW-1317 | NRA-SW-1317 | A2 | Inlet SO at WwTW | SS6840019100 | GB108050014380 | Mole (Taw to Bray) | TRIB OF RIVER TAW |  |  | EDM to be installed by December 2023
South West Water | KINGS NYMPTON CSO | KINGS NYMPTON_CSO_KINGS NYMPTON | 201949 | 201949/CS/01 | A1 | SO on sewer network | SS6837419155 | GB108050014380 | Mole (Taw to Bray) | TONGUE LAKE (S) |  |  | EDM to be installed by December 2023
South West Water | KINGSTON WWTW | KINGSTON STW_SO_KINGSTON | 203413 | 203413 | A2 | Inlet SO at WwTW | SX6385347362 | 266 | N/A | KINGSTON STREAM |  |  | EDM to be installed by December 2023
South West Water | LADOCK VALLEY STW | LADOCK VALLEY STW_SO_TRESILLIAN | 302508 | 302508 | A2 | Inlet SO at WwTW | SW8744046930 | GB108048002350 | Tresillian River (Lower) | TRESILLIAN RIVER ESTUARY(E) |  |  | EDM to be installed by December 2023
South West Water | LAMERTON STW | LAMERTON STW_SO_LAMERTON | 302128 | 302128/CS/01 | A2 | Inlet SO at WwTW | SX4537375668 | GB108047007850 | Lumburn | RIVER LUMBURN (S) |  |  | Jan 2021 | 2019.58 | 109 | 100
South West Water | LANTEGLOS PSCSO/EO | LANTEGLOS SPST_PSEO_LANTEGLOS | 301662 | 301662/PC/01 | A2 | Storm discharge at pumping station | SX1470054450 | GB510804806400 | FOWEY | RIVER FOWEY (E) |  |  | May 2021 | 0 | 0 | 100
South West Water | LAPFORD SEWAGE TREATMENT WORKS | LAPFORD STW_SO_LAPFORD | NPSWQD008007 | NPSWQD008007 | A2 | Inlet SO at WwTW | SS7353007710 | GB108050014640 | Lower River Yeo (Lapford) | THE RIVER DALCH |  |  | EDM to be installed by December 2023
South West Water | LATCHLEY STW | LATCHLEY STW_SO_GUNNISLAKE | 302129 | 302129/CS/01 | A2 | Inlet SO at WwTW | SX4084073830 | GB108047007860 | Lower River Tamar | RIVER TAMAR (S) |  |  | EDM to be installed by December 2023
South West Water | LAWHITTON WWTW CSO | LAWHITTON STW_SO_LAWHITTON | NRA-SW-1341 | NRA-SW-1341 | A2 | Inlet SO at WwTW | SX3594082430 | GB108047007910 | Tamar (River Lyd to River Inny) | TRIB OF RIVER TAMAR |  |  | EDM to be installed by December 2023
South West Water | LEE MILL STW | LEE MILL STW_SSO_PLYMOUTH | NRA-SW-0237 | NRA-SW-0237 | A2 | Storm tank at WwTW | SX6032055624 | GB108047004010 | Lower River Yealm | (S) UNNAMED TRIB RIVER YEALM |  |  | Commissioned in 2018 - full year data expected | 278.13 | 135 | 100
South West Water | LERRYN PSCSO/EO | LERRYN SPST_PSCSOEO_LERRYN | 301663 | 301663/PC/01 | A1 | Storm discharge at pumping station | SX1400056650 | GB510804806400 | FOWEY | RIVER LERRYN (E) |  |  | EDM to be installed by December 2023
South West Water | LEWANNICK STW | LEWANNICK STW_SO_LEWANNICK | 303090 | 303090 | A2 | Inlet SO at WwTW | SX2665080840 | GB108047007700 | Penpont Water | PENPONT(S) |  |  | December 2021 | 0 | 0 | 100
South West Water | LISKEARD STW | LODGEHILL STW_SO_LISKEARD | NRA-SW-3789 | NRA-SW-3789 | A2 | Inlet SO at WwTW | SX2411562962 | GB108048001440 | East Looe River | EAST LOOE RIVER |  |  | EDM to be installed by December 2023
South West Water | ST AUSTELL (LONDON APPRENTICE) PS | LONDON APPRENTICE SPST_PSCSOEO_ST AUSTEL | 303234 | 303234 | A1 | Storm discharge at pumping station | SX0077050100 | GB108048002280 | St Austell River | ST AUSTELL RIVER(S) |  |  | EDM to be installed by December 2023
South West Water | LORDS MEADOW WWTW | LORDS MEADOW STW_CSO_CREDITON | NRA-SW-0215 | NRA-SW-0215 | A1 | SO on sewer network | SS8444300395 | GB108045009090 | Middle Creedy | RIVER YEO/RIVER CREEDY |  |  | EDM to be installed by December 2023
South West Water | LUTTON STW | LUTTON STW_SO_LUTTON | 033125/SF/01 | 033125/SF/01 | A2 | Inlet SO at WwTW | SX5963059310 | GB108047004020 | Piall | (S)RIVER PIALL |  |  | November 2021 | 0 | 0 | 100
South West Water | LUTTON STW | LUTTON STW_SSO_LUTTON | 033125/SS/01 | 033125/SS/01 | A3 | Storm tank at WwTW | SX5963059310 | GB108047004020 | Piall | (S) RIVER PIALL |  |  | November 2021 | 0 | 0 | 100
South West Water | LYDFORD WASTEWATER TRTMENT WORKS | LYDFORD STW_SO_LYDFORD | 303089 | 303089 | A2 | Inlet SO at WwTW | SX5086084800 | GB108047007750 | Upper River Lyd | TRIB RADDON STREAM/GROUND |  |  | Mar 2021 | 1657.39 | 111 | 100
South West Water | THE ANCHORAGE CSO | MAIN ST OPP THE ANCHORAGE_CSO_BLACKAWTON | 201808 | 201808/CS/01 | A1 | SO on sewer network | SX8059050983 | GB108046004930 | The Gara | STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | MELDON ROAD CSO | MELDON RD_CSO_CHAGFORD | 201799 | 201799/CS/01 | A1 | SO on sewer network | SX6988087268 | GB108046008550 | Teign (Upper) | RIVER TEIGN (S) |  |  | EDM to be installed by December 2023
South West Water | #TBC | MERMAID INN_CSO_ST MARYS | #TBC | #TBC | A1 | SO on sewer network | SV 90167 10718 | GB620807080000 | Scilly Isles | #TBC |  |  | EDM to be installed by December 2023
South West Water | MERTON WWTW CSO | MERTON STW_SO_MERTON | NRA-SW-1362 | NRA-SW-1362 | A2 | Inlet SO at WwTW | SS5231811742 | GB108050014260 | Upper River Mere | TRIB OF LITTLE MERE RIVER |  |  | June 2021 | 401 | 54 | 100
South West Water | MEVAGISSEY SS EMERGENCY OVERFLOW | MEVAGISSEY_CSO_MEVAGISSEY | SWWA 85 | SWWA 85 | A1 | SO on sewer network | SX0054044540 | 256 | N/A | TRIB OF MEVAGISSEY STREAM |  |  | EDM to be installed by December 2023
South West Water | MILLBROOK STW | MILLBROOK STW_SO_MILLBROOK | NRA-SW-7829/SS/1 | NRA-SW-7829/SS/1 | A2 | Inlet SO at WwTW | SX4311052430 | GB520804714300 | PLYMOUTH TAMAR | (E) MILLBROOK CREEK |  |  | EDM to be installed by December 2023
South West Water | VICARGE GARDENS CSO MILTON ABBOT | MILTON ABBOT_CSO_MILTON ABBOT | 301860 | 301860/CS/01 | A1 | SO on sewer network | SX4057179152 | GB108047007860 | Lower River Tamar | RIVER TAMAR (S) |  |  | EDM to be installed by December 2023
South West Water | MINIONS STW | MINIONS STW_SO_MINIONS | 302132 | 302132/CS/01 | A2 | Inlet SO at WwTW | SX2611070600 | GB108048002320 | Seaton | TRIB OF RIVER SEATON (S) |  |  | EDM to be installed by December 2023
South West Water | MINIONS CSO | MINIONS_CSO_MINIONS | 301861 | 301861/CS/01 | A1 | SO on sewer network | SX2607371146 | GB108048002320 | Seaton | EAST LOOE RIVER (S) |  |  | EDM to be installed by December 2023
South West Water | WWTW AT MORCHARD BISHOP | MORCHARD BISHOP STW_SO_MORCHARD BISHOP | 003126/SF/01 | 3126 | A2 | Inlet SO at WwTW | SS7652007770 | GB108050008290 | Knighty Brook | (S) TRIB OF LAKE PEPPER |  |  | June 2021 | 203.98 | 42 | 100
South West Water | MOYLE ROAD CSO | MOYLE RD_CSO_PADSTOW | 302975 | 302975 | A1 | SO on sewer network | SW9218074790 | GB530804906600 | CAMEL | CAMEL ESTUARY (E) |  |  | Commissioned pre-2016 - full year data expected | 4.92 | 18 | 100
South West Water | MUTTON COVE PUMPING STATION | MUTTON COVE SPS_PSCSOEO_PLYMOUTH | 300824 | 300824 | A1 | Storm discharge at pumping station | SX4528853967 | GB520804714300 | PLYMOUTH TAMAR | RIVER TAMAR (ESTUARINE) |  |  | Commissioned in 2016 - full year data expected | 65.75 | 45 | 100
South West Water | BODMIN NANSTALLON WWTW | NANSTALLON STW_SO_BODMIN | NRA-SW-6959 | NRA-SW-6959 | A2 | Inlet SO at WwTW | SX0449567023 | GB108049000040 | St Lawrence Stream | RIVER CAMEL/ST LAWRENCE STR |  |  | EDM to be installed by December 2023
South West Water | NEW GRIMSBY PUMPING STATION | NEW GRIMSBY SPS_PSCSOEO_TRESCO | EPRDB3293RV | EPR/DB3293RV | A1 | Storm discharge at pumping station | SV8870215296 | GB620807080000 | Scilly Isles | ATLANTIC OCEAN |  |  | EDM to be installed by December 2023
South West Water | NEWTON ST CYRES STW | NEWTON ST CYRES STW_SO_NEWTON ST CYRES | NRA-SW-0247 | NRA-SW-0247 | A2 | Inlet SO at WwTW | SX8862097750 | GB108045009070 | Lower Creedy | (S) RIVER CREEDY |  |  | Feb 2021 | 0 | 0 | 100
South West Water | NORTH MOLTON STW | NORTH MOLTON STW_SSO_NORTH MOLTON | SWWA 224 | SWWA 224 | A2 | Storm tank at WwTW | SS7450029700 | GB108050019970 | Mole (Source to Burcombe Stream) | RIVER MOLE |  |  | Mar 2021 | 1872.26 | 167 | 100
South West Water | NORTH TAWTON PSCSO/EO | NORTH TAWTON SPST_PSCSOEO_NORTH TAWTON | 201668 | 201668/PC/01 | A1 | Storm discharge at pumping station | SS6569201709 | GB108050008250 | Taw (Source to Bullow Brook) | RIVER TAW (S) |  |  | EDM to be installed by December 2023
South West Water | NORTHLEW SEWAGE TREATMENT WORKS | NORTHLEW STW_SSO_HATHERLEIGH | 200413 | 200413/SS/01 | A2 | Storm tank at WwTW | SX5035098910 | GB108050008140 | Northlew Stream | NORTHLEW STRM AND TRIBUTARY(S) |  |  | June 2021 | 579.34 | 49 | 100
South West Water | OVERSEAS ESTATE WEST PS | O/SEAS EST W SPS_PSCSOEO_STOKE FLEMING | 203452 | 203452 | A1 | Storm discharge at pumping station | SX8618047930 | GB620806110002 | Devon South | ENGLISH CHANNEL (COASTAL) |  |  | EDM to be installed by December 2023
South West Water | HAM LANE STORM TANK CSO | OFF HAM LN, HAM WOOD_CSO_PLYMOUTH | 302612 | 302612 | A1 | SO on sewer network | SX4608857969 | 73 | N/A | HAM BROOK(S) |  |  | EDM to be installed by December 2023
South West Water | OFFWELL WASTEWATER TREATMENT WORKS | OFFWELL STW_SSO_OFFWELL | 200366 | 200366 | A2 | Storm tank at WwTW | SY1919098870 | GB108045008840 | Offwell Brook | TRIB OF OFFWELL BROOK |  |  | June 2021 | 145.46 | 27 | 92
South West Water | OLD COACH ROAD | OLD COACH RD_CSO_LANIVET | 301686 | 301686/CS/01 | A1 | SO on sewer network | SX0373464702 | GB108049000030 | Lanivet Stream | RIVER CAMEL (S) |  |  | EDM to be installed by December 2023
South West Water | OLD TIVERTON ROAD CSO | OLD TIVERTON RD/BLAGDON_CSO_CREDITON | 201868 | 201868/CS/01 | A1 | SO on sewer network | SS8381000372 | GB108045009090 | Middle Creedy | STREAM(S) |  |  | EDM to be installed by December 2023
South West Water | OTTERY ST MARY ATTENUATION TANK | Ottery St Mary Atten Tank (settled storm) | DRA 96 | DRA 96 | A2 | SO on sewer network | SY0946595107 | GB108045009170 | Lower River Otter | THE RIVER OTTER |  |  | EDM to be installed by December 2023
South West Water | 139 OUTLAND ROAD CSO | OUTLAND ROAD_CSO_PLYMOUTH | 301761 | 301761/CS/01 | A1 | SO on sewer network | SX4739157004 | GB520804714300 | PLYMOUTH TAMAR | STONEHOUSE CREEK (E) |  |  | EDM to be installed by December 2023
South West Water | OVERSEAS ESTATE EAST PS | OVERSEAS ESTATE EAST SPS_PSCSOEO_STOKE F | 203453 | 203453 | A1 | Storm discharge at pumping station | SX8641048010 | GB620806110002 | Devon South | ENGLISH CHANNEL (COASTAL) |  |  | EDM to be installed by December 2023
South West Water | PAR SEWAGE TREATMENT WORKS | PAR STW_SSO_ST AUSTELL | 031299/SS/01 | 031299/SS/01 | A2 | Inlet SO at WwTW | SX0685052680 | GB620806110001 | St Austell | (C) ST AUSTELL BAY |  |  | Commissioned pre-2016 - full year data expected | 141.1 | 10 | 100
South West Water | PARIS STREET CSO | PARIS STREET_CSO_EXETER | 201895 | 201895 | A1 | SO on sewer network | SX9255092840 | GB108045009040 | Exe (Creedy to Estuary) | RIVER EXE VIA SWS |  |  | EDM to be installed by December 2023
South West Water | PARKHAM STW | PARKHAM STW_SO_PARKHAM | NRA-SW-6627 | NRA-SW-6627 | A2 | Inlet SO at WwTW | SS3906021360 | GB108050014470 | Upper River Yeo (Bideford) | (S) RIVER YEO |  |  | June 2021 | 3.84 | 12 | 100
South West Water | PARKHAM STW | PARKHAM STW_SSO_PARKHAM | NRA-SW-6627 | NRA-SW-6627 | A3 | Storm tank at WwTW | SS3906021360 | GB108050014470 | Upper River Yeo (Bideford) | (S) RIVER YEO |  |  | June 2021 | 407.86 | 30 | 100
South West Water | PARRACOMBE STW | PARRACOMBE STW_SO_PARRACOMBE | NRA-SW-0411 | NRA-SW-0411 | A2 | Inlet SO at WwTW | SS6646044990 | GB108051020500 | Heddon | (S) RIVER HEDDON |  |  | June 2021 | 1541.63 | 94 | 100
South West Water | PAYHEMBURY STW | PAYHEMBURY STW_SSO_PAYHEMBURY | SWWA 2498 | SWWA 2498 | A2 | Storm tank at WwTW | ST0873001220 | GB108045009200 | Tale | PAYHEMBURY STREAM (S) |  |  | Commissioned in 2017 - full year data expected | 499.33 | 95 | 100
South West Water | PETROCKSTOWE STW | PETROCKSTOWE STW_SO_PETROCKSTOW | 202205 | 202205/CS/01 | A2 | Inlet SO at WwTW | SS5125010020 | GB108050014190 | Little Mere River | TRIB OF LITTLE MERE RIVER(S) |  |  | June 2021 | 620.06 | 74 | 100
South West Water | OLD LAIRA ROAD JUNCTION CSO | PLYMOUTH ROAD/EMBANKMENT RD_PLYMOUTH | 301765 | 301765 | A2 | SO on sewer network | SX5088055980 | GB520804714300 | PLYMOUTH TAMAR | RIVER PLYM (ESTUARINE) |  |  | Commissioned in 2016 - full year data expected | 0.56 | 4 | 100
South West Water | PLYMTREE STW | PLYMTREE STW_SSO_PLYMTREE | NRA-SW-3744 | NRA-SW-3744 | A2 | Storm tank at WwTW | ST0491002800 | GB108045008860 | Upper Clyst | RIVER WEAVER |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 100
South West Water | POLBATHIC VILLAGE PS | POLBATHIC VILLAGE SPS_PSCSOEO_SALTASH | 303504 | 303504 | A1 | Storm discharge at pumping station | SX3478056920 | 72 | N/A | POLBATHIC STREAM(S) |  |  | EDM to be installed by December 2023
South West Water | PONSANOOTH STW SSO | PONSANOOTH STW_SO_PONSANOOTH | NRA-SW-1484 | NRA-SW-1484 | A2 | Inlet SO at WwTW | SW7661637766 | GB108048001140 | Kennal | RIVER KENNAL |  |  | EDM to be installed by December 2023
South West Water | PORT GAVERNE CSO | PORT GAVERNE_CSO_PORT GAVERNE | 301688 | 301688/CS/01 | A1 | SO on sewer network | SX0031080803 | 234 | N/A | COASTAL STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | PORT ISAAC WWTW CSO | PORT ISAAC STW_SO_PORT ISAAC | 2895/71 | 2895/71 | A2 | Inlet SO at WwTW | SW9977080400 | GB610807680002 | Cornwall North | PORT ISSAC BAY, ATLANTIC |  |  | Mar 2021 | 0.05 | 1 | 88 | Comms failure / issue | Resolved - October
South West Water | BAMALUZ POINT STORM WATER & EO | PORTHGWIDDEN SPST_PSCSOEO_ST IVES | NRA-SW-2266 | NRA-SW-2266 | A1 | Storm discharge at pumping station | SW5228141020 | GB610807680001 | Lands End to Trevose Head | ST IVES BAY |  |  | Commissioned pre-2016 - full year data expected | 2.56 | 5 | 100
South West Water | THE POST OFFICE CSO | POST OFFICE_CSO_SOUTH ZEAL | 201716 | 201716/CS/01 | A1 | SO on sewer network | SX6516993524 | GB108050008250 | Taw (Source to Bullow Brook) | STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | POUNDSHILL PSCO/EO | POUNDS HILL SPS_PSCSOEO_HOLCOMBE ROGUS | 202172 | 202172/PC/01 | A1 | Storm discharge at pumping station | ST0606918853 | GB108045015020 | Spratford Stream | STREAM |  |  | EDM to be installed by December 2023
South West Water | PRAZE AN BEEBLE STW | PRAZE AN BEEBLE STW_SO_PRAZE AN BEEBLE | NRA-SW-7821 | NRA-SW-7821 | A2 | Inlet SO at WwTW | SW6335035870 | GB108049000560 | Roseworthy Stream | (S) PRAZE RIVER |  |  | June 2021 | 0 | 0 | 50 | Sensor failure / issue | N/A - Ongoing investigation
South West Water | PRAZE AN BEEBLE STW | PRAZE AN BEEBLE STW_SSO_PRAZE AN BEEBLE | NRA-SW-7821 | NRA-SW-7821 | A3 | Storm tank at WwTW | SW6335035870 | GB108049000560 | Roseworthy Stream | (S) PRAZE RIVER |  |  | April 2021 | 368.45 | 18 | 100
South West Water | PRINCETOWN SEWAGE TREATMENT WORKS | PRINCETOWN STW_SO_PRINCETOWN | 201064 | 201064/CS/01 | A2 | Inlet SO at WwTW | SX5969774273 | GB108046008370 | Blackbrook River | BLACKBROOK RIVER(S) |  |  | EDM to be installed by December 2023
South West Water | PRINCETOWN SEWAGE TREATMENT WORKS | PRINCETOWN STW_SSO_PRINCETOWN | 201064 | 201064/SS/01 | A2 | Storm tank at WwTW | SX5969774273 | GB108046008370 | Blackbrook River | BLACKBROOK RIVER(S) |  |  | EDM to be installed by December 2023
South West Water | PYWORTHY SEWAGE TREATMENT WORKS | PYWORTHY STW_SSO_PYWORTHY | 302417 | 302417 | A2 | Storm tank at WwTW | SS3088003210 | GB108047008070 | Derril Water | DERRIL WATER(S) |  |  | Commissioned in 2020 - full year data expected | 4570.3 | 238 | 100
South West Water | R/O GARAGES LANHYDROCK ROAD CSO | R/O LANHYDROCK ROAD_CSO_PLYMOUTH | 301736 | 301736/CS/01 | A1 | SO on sewer network | SX4906854805 | GB520804714300 | PLYMOUTH TAMAR | RIVER PLYM (E) |  |  | EDM to be installed by December 2023
South West Water | RAILWAY STATION COMBINED SEWER OF | RAILWAY STATION_CSO_AXMINSTER | DRA 1563 | DRA 1563 | A1 | SO on sewer network | SY2937098305 | GB108045008870 | Lower Axe | RIVER AXE |  |  | EDM to be installed by December 2023
South West Water | RATTERY WWTW CSO | RATTERY STW_SO_RATTERY | NRA-SW-1494 | NRA-SW-1494 | A2 | Inlet SO at WwTW | SX7432061620 | GB108046005160 | Bidwell Brook | BIDWELL BROOK |  |  | EDM to be installed by December 2023
South West Water | SANDFORD ROSE & CROWN CSO | ROSE AND CROWN PUB_CSO_SANDFORD | 203074 | 203074 | A1 | SO on sewer network | SS8276002309 | GB108045009090 | Middle Creedy | THE SANDFORD STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | SALCOMBE REGIS WWTW CSO | SALCOMBE REGIS STW_SO_SALCOMBE REGIS | NRA-SW-1505 | NRA-SW-1505 | A2 | Inlet SO at WwTW | SY1472088650 | 408 | N/A | SALCOMBE REGIS STREAM |  |  | EDM to be installed by December 2023
South West Water | SAMPFORD COURTNEY STW | SAMPFORD COURTENAY STW_SO_SAMPFORD COURT | NRA-SW-3659 | NRA-SW-3659 | A2 | Inlet SO at WwTW | SS6331301145 | GB108050014090 | Hole Brook | TRIBUTARY TO THE HOLE BROOK |  |  | EDM to be installed by December 2023
South West Water | SAMPFORD COURTNEY STW | SAMPFORD COURTENAY STW_SSO_SAMPFORD COUR | NRA-SW-3658 | NRA-SW-3658 | A3 | Storm tank at WwTW | SS6331301145 | GB108050014090 | Hole Brook | TRIBUTARY TO THE HOLE BROOK |  |  | Mar 2021 | 0 | 0 | 100
South West Water | SEA LAWNS OUTFALL CSO, DAWLISH | SEA LAWNS SPS_PSCSOEO_DAWLISH | 200828 | 200828 | A1 | Storm discharge at pumping station | SX9674077100 | GB650806420000 | Lyme Bay West | LYME BAY(C) |  |  | EDM to be installed by December 2023
South West Water | SEA LAWNS PUMPING STATION | SEA LAWN TERRACE_FEO_DAWLISH | 200827 | 200827 | A1 | Storm discharge at pumping station | SX9674077080 | GB650806420000 | Lyme Bay West | LYME BAY |  |  | EDM to be installed by December 2023
South West Water | SEARLE STREET CSO | SEARLE ST_CSO_CREDITON | 201878 | 201878/CS/01 | A1 | SO on sewer network | SS8307000051 | GB108045009280 | Lower Yeo (Creedy) | STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | SHEVIOCK STW SO | SHEVIOCK S T SEPTNK_SO_SHEVIOCK | NRA-SW-1518 | NRA-SW-1518 | A2 | Inlet SO at WwTW | SX3740154900 | 72 | N/A | RIVER LYNHER |  |  | Commissioned in 2019 - full year data expected | 293.69 | 17 | 97.92
South West Water | SHOBROOKE PS | SHOBROOKE SPST_PSCSOEO_SHOBROOKE | NRA-SW-4101 | NRA-SW-4101 | A1 | Storm discharge at pumping station | SS8712001320 | GB108045009100 | Shobrooke Lake | SHOBROOKE LAKE |  |  | EDM to be installed by December 2023
South West Water | MOUSEHOLE HARBOUR (SOUTH SLIP) CSO | SOUTH SLIP_CSO_MOUSEHOLE | 2894/103 | 2894/103 | A1 | SO on sewer network | SW4695026230 | GB650806340000 | Penzance | MOUNTS BAY ENGLISH CHANNEL |  |  | EDM to be installed by December 2023
South West Water | SOUTH STREET CSO | SOUTH ST_CSO_SOUTH MOLTON | 201941 | 201941/CS/01 | A1 | SO on sewer network | SS7137525488 | GB108050013950 | Nadrid Water | TRIBUTARY OF NADRID WATER (S) |  |  | EDM to be installed by December 2023
South West Water | SPARKWELL WASTEWATER TREATMENT WORK | SPARKWELL STW_SO_SPARKWELL | 15/47/1/P/9 | 15/47/1/P/9 | A2 | Inlet SO at WwTW | SX5832657082 | GB108047004000 | Silverbridge Lake | TRIBUTARY OF SILVERBRIDGE LAKE |  |  | EDM to be installed by December 2023
South West Water | SPARRY LANE CSO | SPARRY LN_CSO_CARHARRICK | 301813 | 301813/CS/01 | A1 | SO on sewer network | SW7349141445 | GB108048001150 | Hicks Mill Stream | CARNON RIVER (S) |  |  | EDM to be installed by December 2023
South West Water | SPREYTON STW | SPREYTON STW_SO_SPREYTON | 203380 | 203380 | A2 | Inlet SO at WwTW | SX6987797485 | GB108050008270 | Upper River Yeo (Lapford) | COOMBE STREAM(S) |  |  | December 2021 | 0 | 0 | 100
South West Water | SPREYTON STW | SPREYTON STW_SSO_SPREYTON | 203380 | 203380 | A3 | Storm tank at WwTW | SX6987797485 | GB108050008270 | Upper River Yeo (Lapford) | COOMBE STREAM(S) |  |  | December 2021 | 0 | 0 | 100
South West Water | ST BREWARD STW | ST BREWARD STW_SSO_ST BREWARD | NRA-SW-6746 | NRA-SW-6746 | A2 | Storm tank at WwTW | SX0913076180 | GB108049006980 | Camel (De Lank to Stannon) | (S) RIVER CAMEL |  |  | Mar 2021 | 0 | 0 | 100
South West Water | ST COLUMB STW | ST COLUMB STW_SSO_ST COLUMB | 303683 | 303683 | A2 | Inlet SO at WwTW | SW9049064000 | GB108049000070 | Menalhyl | RIVER MENAHYL |  |  | Commissioned pre-2016 - full year data expected | 60.91 | 38 | 100
South West Water | ST MARTINS LANE CSO | ST MARTINS LANE_CSO_CREDITON | 201877 | 201877/CS/01 | A1 | SO on sewer network | SS8265400615 | GB108045009090 | Middle Creedy | STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | ST MELLION PUMPING STATION | ST MELLION COTTS_CSO_SALTASH | 301878 | 301878/CS/01 | A1 | SO on sewer network | SX3893065430 | 71 | N/A | STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | ST MELLION PUMPING STATION | ST MELLION_PSCSOEO_ST MELLION | 302501 | 302501 | A1 | Storm discharge at pumping station | SX3893065430 | 71 | N/A | ST MELLION STREAM(S) |  |  | EDM to be installed by December 2023
South West Water | ST NEOT STW | ST NEOT STW_SO_ST NEOT | NRA-SW-3674 | NRA-SW-3674 | A2 | Inlet SO at WwTW | SX1880767389 | GB108048007640 | St Neot River | ST NEOT RIVER |  |  | EDM to be installed by December 2023
South West Water | STATION ROAD PSCSO/EO WILLAND | STATION ROAD SPS_PSCSOEO_WILLAND | 202175 | 202175/PC/01 | A1 | Storm discharge at pumping station | ST0332111417 | GB108045015020 | Spratford Stream | SPRATFORD STREAM |  |  | EDM to be installed by December 2023
South West Water | STIBB SEWAGE TREATMENT WORKS | STIBB STW_SO_STIBB | 300394 | 300394 | A2 | Inlet SO at WwTW | SS2241010840 | GB108049013760 | Coombe Valley Stream | TRIB OF COOMBE VALLEY STR (S) |  |  | EDM to be installed by December 2023
South West Water | STICKLEPATH BRIDGE CSO | STICKLEPATH BRIDGE_CSO_STICKLEPATH | 201713 | 201713/CS/01 | A1 | SO on sewer network | SX6432494019 | GB108050008250 | Taw (Source to Bullow Brook) | RIVER TAW (S) |  |  | EDM to be installed by December 2023
South West Water | STOODLEIGH STW | STOODLEIGH STW_SO_STOODLEIGH | NRA-SW-1567 | NRA-SW-1567 | A2 | Inlet SO at WwTW | SS9250019000 | GB108045015050 | Exe (Barle to Culm) | STOODLEIGH STREAM |  |  | EDM to be installed by December 2023
South West Water | SUNGIRT LANE CSO | SUNGIRT LANE_CSO_LISKEARD | 303471 | 303471 | A1 | Storm discharge at pumping station | SX2519264255 | GB108048001440 | East Looe River | TRIBUTARY OF EAST LOOE RIVER |  |  | Commissioned pre-2016 - full year data expected | 43.22 | 26 | 100
South West Water | STICKLEPATH BRIDGE CSO | TAWSIDE HOUSE_CSO_STICKLEPATH | 201713 | 201712/CS/01 | A1 | SO on sewer network | SX6432494019 | GB108050008250 | Taw (Source to Bullow Brook) | RIVER TAW (S) |  |  | EDM to be installed by December 2023
South West Water | TEDBURN ST MARY STW | TEDBURN ST MARY STW_SO_TEDBURN ST MARY | 203478 | 203478 | A2 | Inlet SO at WwTW | SX8245093900 | GB108045009220 | Culvery River | LILLY BROOK(S) |  |  | EDM to be installed by December 2023
South West Water | TEDBURN ST MARY STW | TEDBURN ST MARY STW_SSO_TEDBURN ST MARY | 203478 | 203478 | A3 | Storm tank at WwTW | SX8245093900 | GB108045009220 | Culvery River | LILLY BROOK(S) |  |  | EDM to be installed by December 2023
South West Water | THE HAM PS TANK & CSO - SIDMOUTH | THE HAM SPST_PSCSOEO_SIDMOUTH2 | 200835 | 200835/PC/01 | A1 | Storm discharge at pumping station | SY1284087350 | GB650806420000 | Lyme Bay West | (S) RIVER SID AND (C) LYME BAY |  |  | EDM to be installed by December 2023
South West Water | THE HAM PS TANK & CSO - SIDMOUTH | THE HAM SPST_PSEO_SIDMOUTH | 200835 | 200835/PC/01 | A2 | Storm discharge at pumping station | SY1284087350 | GB650806420000 | Lyme Bay West | (S) RIVER SID AND (C) LYME BAY |  |  | EDM to be installed by December 2023
South West Water | THE OLD DAIRY CSO | THE OLD DAIRY NORTH ST_CSO_NORTH TAWTON | 201732 | 201732/CS/01 | A1 | SO on sewer network | SS6642501940 | GB108050008250 | Taw (Source to Bullow Brook) | STREAM (S) |  |  | EDM to be installed by December 2023
South West Water | TREBULLETT STW | TREBULLETT STW_SO_TREBULLETT | NRA-SW-5050 | NRA-SW-5050 | A2 | Inlet SO at WwTW | SX3225077150 | GB108047007890 | Lower River Inny | THE RIVER INNY |  |  | EDM to be installed by December 2023
South West Water | TREKNOW STW | TREKNOW STW_SO_TREBARWITH | CRA 1 | CRA 1 | A2 | Inlet SO at WwTW | SX0555486498 | 234 | N/A | (S) TREBARWITH STREAM |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100
South West Water | TRUSHAM SEWAGE TREATMENT WORKS | TRUSHAM STW_SO_TEIGN VALLEY | 203566 | 203566 | A2 | Inlet SO at WwTW | SX8520082130 | GB108046008540 | Teign (Lower) | TRUSHAM STREAM(S) |  |  | EDM to be installed by December 2023
South West Water | UGBOROUGH STW | UGBOROUGH STW_SO_UGBOROUGH | NRA-SW-6965 | NRA-SW-6965 | A2 | Inlet SO at WwTW | SX6753055510 | GB108046005110 | Lud Brook | (S) TRIB OF LUD BROOK |  |  | August 2021 | 15.28 | 19 | 100
South West Water | UGBOROUGH STW | UGBOROUGH STW_SSO_UGBOROUGH | NRA-SW-6965 | NRA-SW-6965 | A3 | Storm tank at WwTW | SX6753055510 | GB108046005110 | Lud Brook | (S) TRIB OF LUD BROOK |  |  | Mar 2021 | 161.26 | 17 | 100
South West Water | VERYAN STW | VERYAN STW_SO_VERYAN | NRA-SW-6742 | NRA-SW-6742 | A2 | Inlet SO at WwTW | SW9136039810 | 403 | N/A | CARNE STREAM |  |  | Mar 2021 | 6.75 | 16 | 93
South West Water | WALKHAMPTON WWTW SSO | WALKHAMPTON STW_SSO_WALKHAMPTON | NRA-SW-1679 | NRA-SW-1679 | A2 | Storm tank at WwTW | SX5310170100 | GB108047007870 | Walkham | TRIB OF RIVER WALKHAM |  |  | Mar 2021 | 1122.27 | 68 | 100
South West Water | WASHFIELD STW | WASHFIELD STW_SO_TIVERTON | 202212 | 202212/CS/01 | A2 | Inlet SO at WwTW | SS9354015150 | GB108045015050 | Exe (Barle to Culm) | TRIBUTARY OF RIVER EXE(S) |  |  | EDM to be installed by December 2023
South West Water | WEEK ST MARY STW | WEEK ST MARY STW_SO_WEEK ST MARY | NRA-SW-6685 | NRA-SW-6685 | A2 | Inlet SO at WwTW | SX2371098050 | GB108049007250 | Upper River Neet | (S) WEEK BROOK |  |  | August 2021 | 874.13 | 136 | 100
South West Water | WEST BUCKLAND STW | WEST BUCKLAND STW_SO_BARNSTAPLE | 202213 | 202213/CS/01 | A2 | Inlet SO at WwTW | SS6588031100 | GB108050019910 | Bray (Mole to Hole Water) | TRIBUTARY OF RIVER MOLE(S) |  |  | EDM to be installed by December 2023
South West Water | WEST CHARLETON STW | WEST CHARLETON STW_SO_CHARLETON | 203206 | 203206 | A2 | Inlet SO at WwTW | SX7525042380 | 69 | N/A | CHARLETON STREAM(S) |  |  | EDM to be installed by December 2023
South West Water | WEST LANE CSO | WEST ST_CSO_SHEEPWASH | 201943 | 201943/CS/01 | A1 | SO on sewer network | SS4844306397 | GB108050013930 | Torridge (Combe Lake to Lew) | TRIB OF R. TORRIDGE (S) |  |  | EDM to be installed by December 2023
South West Water | WEST DOWN STW | WESTDOWN STW_SO_WEST DOWN | NRA-SW-0423 | NRA-SW-0423 | A2 | Inlet SO at WwTW | SS5050042300 | GB108050020060 | Bradwell Stream | UNNAMED TRIB RIVER CAEN |  |  | August 2021 | 223.19 | 90 | 100
South West Water | WEST DOWN STW | WESTDOWN STW_SSO_WEST DOWN | NRA-SW-0423 | NRA-SW-0423 | A3 | Storm tank at WwTW | SS5050042300 | GB108050020060 | Bradwell Stream | UNNAMED TRIB RIVER CAEN |  |  | EDM to be installed by December 2023
South West Water | WHIDDON DOWN STW | WHIDDON DOWN STW_SO_WHIDDON DOWN | 203600 | 203600 | A2 | Inlet SO at WwTW | SX6908092370 | GB108046008570 | Fingle Brook | FINGLE BROOK(S) |  |  | EDM to be installed by December 2023
South West Water | WILCOVE STW | WILCOVE SPST_PSCSOEO_TORPOINT | 302738 | 302738 | A1 | Storm discharge at pumping station | SX4300056290 | GB520804714300 | PLYMOUTH TAMAR | THE HAMOAZE(S) |  |  | EDM to be installed by December 2023
South West Water | WILLOWDALE PSCSO/EO | WILLOWDALE CLOSE SPS_PSCSOEO_HONITON | 202182 | 202182/PC/01 | A1 | Storm discharge at pumping station | ST1556200923 | GB108045009180 | Middle River Otter | TRIB OF RIVER OTTER (S) |  |  | EDM to be installed by December 2023
South West Water | WILMINGTON STW | WILMINGTON STW_SO_WILMINGTON | NRA-SW-2877 | NRA-SW-2877 | A2 | Inlet SO at WwTW | ST2161000010 | GB108045008880 | Umborne Brook | (S) UMBORNE BROOK |  |  | August 2021 | 189.78 | 19 | 72 | Comms failure / issue | Resolved - November
South West Water | WINKLEIGH WASTEWATER TREATMENT WRKS | WINKLEIGH STW_SSO_WINKLEIGH | 203662 | 203662 | A2 | Storm tank at WwTW | SS6366007680 | GB108050014170 | Bullow Brook | BULLOW BROOK(S) |  |  | EDM to be installed by December 2023
South West Water | WOOLFARDISWORTHY STW | WOOLSERY STW_SSO_WOOLFARDISWORTHY | NRA-SW-0272 | NRA-SW-0272 | A2 | Storm tank at WwTW | SS3402020930 | GB108050014370 | Dipple Water | (S) TRIB CRANFORD WATER |  |  | Jan 2021 | 604.89 | 44 | 100
South West Water | YARROW BANK PUMPING STATION | YARROW BANK SPS_PSCSOEO_KINGSWEAR | 200472/PC/01 | 200472/PC/01 | A1 | Storm discharge at pumping station | SX8843050800 | GB510804605900 | DART | DART ESTUARY (TIDAL) |  |  | EDM to be installed by December 2023
South West Water | YEOLMBRIDGE CSO | YEOLMBRIDGE_CSO_YEOLMBRIDGE | 301899 | 301899/CS/01 | A1 | SO on sewer network | SX3176487400 | GB108047007981 | Lower River Ottery | RIVER YEOLM (S) |  |  | EDM to be installed by December 2023
South West Water | ZEAL MONACHORUM STW | ZEAL MONACHORUM STW_SSO_ZEAL MONACHORUM | NRA-SW-3519 | NRA-SW-3519 | A2 | Storm tank at WwTW | SS7243203935 | GB108050008270 | Upper River Yeo (Lapford) | RIVER YEO |  |  | Mar 2021 | 0 | 0 | 100
South West Water | St Just (Tregeseal 1) | TREGESEAL STW_SO_ST JUST | SWWA 2110 | 302141/CS/01 | A2 | Inlet SO at WwTW | SW 3675 3195 | 230 | #N/A | (S) Tregeseal River |  |  | EDM to be installed by December 2023

## Drop Downs - SO
Storm discharge asset type | Initial EDM Commission Date | EDM Operation - Reporting percentage - Primary Reason <90% | EDM Operation - Action taken / planned - Status & Timeframe | High Spill Frequency - Operational Review - Primary Reason (Asset Maintenance) | High Spill frequency - Action taken / planned - Status & Timeframe | High Spill Frequency - Environmental Enhancement - Planning Position (Hydraulic Capacity)
SO on sewer network | Installed but not yet commissioned | Access - Unable to retrieve data from non-telemetry data logger (NB: not to be used for delayed access to fix existing fault) | Scheduled | Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue | Scheduled | SOAF N/A - Proposed SFTP (overflow previously improved)
Storm discharge at pumping station | Commissioned in 2020 - full year data expected | Capital / maintenance works affect EDM operation | Resolved - January | Performance - Sewer collapse (partial / full) - infrastructure issue | Resolved - January | Stage 1a: Confirmed "exceptional weather" issue
Inlet SO at WwTW | Commissioned in 2019 - full year data expected | Comms failure / issue | Resolved - Feburary | Performance - GW inundation | Resolved - Feburary | Stage 1b: Confirmed "asset maintenance" issue
Storm tank at WwTW | Commissioned in 2018 - full year data expected | EDM not yet installed | Resolved - March | Performance - Infiltration | Resolved - March | Stage 1c: Confirmed "hydraulic issue"
Other storm discharge asset type | Commissioned in 2017 - full year data expected | EDM installed - not yet commissioned | Resolved - April | Performance - Asset power failure | Resolved - April | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
| Commissioned in 2016 - full year data expected | Installation set-up/design issue | Resolved - May | Performance - Pump failure / issue | Resolved - May | U_INV driver - Stage 4: Cost beneficial outcome not yet determined
| Commissioned pre-2016 - full year data expected | Power failure / issue | Resolved - June | Performance - Other maintenance / capital works (e.g. jetting) | Resolved - June | U_INV driver - Stage 4: No cost beneficial solution
| Jan 2021 | Sensor failure / issue | Resolved - July | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Resolved - July | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP7 or Green Recovery
| Feb 2021 | Telemetry or data archiving failure / issue | Resolved - August | Data collection - EDM non-representative location | Resolved - August | U_IMP4 driver - Stage 4: Potential spill reduction scheme - Not yet on current WINEP/AMP7 or Green Recovery
| Mar 2021 | No longer operational as an overflow - permit revoked or to be revoked | Resolved - September | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | Resolved - September | N/A - Operational solution applied
| April 2021 |  | Resolved - October | Data collection - Tidal / river inundation | Resolved - October
| May 2021 |  | Resolved - November | Not asset maintenance - Hydraulic capacity | Resolved - November
| June 2021 |  | Resolved - December |  | Resolved - December
| July 2021 |  | N/A - Ongoing investigation |  | N/A - Ongoing investigation
| August 2021 |  | N/A - EDM to be installed by December 2023 |  | N/A - Hydraulic capacity
September 2021
October 2021
November 2021
December 2021
EDM to be installed by December 2023